## Data Entry
Power Consumption Cost of Fixed Speed versus Damper / Valve, Inlet Vane Guide and ASD
Motor, Load and System Info |  |  |  | Load Profile
Motor HP | 500 |  |  | Operation | Percentage
FL RPM | 1771 |  |  | Hours | of Flow
| FL | 3/4 | 1/2 | 0 | 100%
Motor Efficiencies | 92% | 91% | 90% | 2 | 90%
Load at 100% flow | 500 | (HP) |  | 6 | 80%
Power Cost | 3.43 | (cents / KWHR) |  | 7 | 70%
Operating hrs/day | 24 |  |  | 3 | 60%
Days per year | 365 |  |  | 5 | 50%
|  |  |  | 1 | 40%
Cost Comparison per year |  |  |  | 0 | 30%
Fixed Speed | 121820.1783 |  |  | 0 | 20%
Outlet Damper or Valve | 108665.5324 |  |  | 0 | 10%
Inlet Guide Vane | 82217.4052 |  |  | 0 | 0%
ASD | 44643.9145 |  |  | 24
Simple Payback
ASD Cost | 50000
Install Cost | 24000 |  | Yearly Energy Savings
ASD vs Fixed Speed | 0.95884 | (years) |  | ASD vs Fixed Speed | 77176.2638
ASD vs Outlet damper | 1.1559 | (years) |  | ASD vs Outlet damper | 64021.6179
ASD vs Valve (on pump) | 1.1559 | (years) |  | ASD vs Valve (on pump) | 64021.6179
ASD vs Inlet Guide Vane | 1.9695 | (years) |  | ASD vs Inlet Guide Vane | 37573.4907
Note - Eddy Current Coupling efficiency profile is very similar to Inlet Guide Vane control.
Note on I7: If a different value is desired, input value (e.g. change 100% to 96%) Note value must be >90%
Note on I8: If a different value is desired, input value (e.g. change 90% to 86%) Note value must be >90% & <100%
Note on I9: If a different value is desired, input value (e.g. change 80% to 76%) Note value must be >80% & <90%
Note on I10: If a different value is desired, input value (e.g. change 70% to 76%) Note value must be >70% & <80%
Note on I11: If a different value is desired, input value (e.g. change 60% to 66%) Note value must be >60% & <70%
Note on I12: If a different value is desired, input value (e.g. change 50% to 56%) Note value must be >50% & <60%
Note on I13: If a different value is desired, input value (e.g. change 40% to 46%) Note value must be >40% & <50%
Note on I14: If a different value is desired, input value (e.g. change 30% to 36%) Note value must be >30% & <40%
Note on I15: If a different value is desired, input value (e.g. change 20% to 26%) Note value must be >20% & <30%
Note on I16: If a different value is desired, input value (e.g. change 10% to 16%) Note value must be >10% & <20%
Note on I17: If a different value is desired, input value (e.g. change 0% to 6%) Note value must be >0% & <10%
Note on C9: Input actual loading of motor at full speed. Normally a motor is not loaded to exactly 100% of the motor's nameplate HP. If actual load is unknown, enter motor nameplate HP. This must be filled in or the calculator will not work.

## 460V EQPIII Data
460V TOSHIBA EQPIII-XS MOTOR DATA | [40 empty] | Data subject to change without notice |  |  |  | 1.3
Note 900RPM data is Standard Efficiency Data | [16 empty] | Min. |  | Min. | [15 empty] | EQP3
[17 empty] | Guar. |  | Guar. |  |  |  |  | STALL | STALL | Max. |  |  |  |  | -Note #1- |  | TIME | Std | Max. | Max. |  |  |  | Temp. | Temp. | Type | Min. | Max
Rated |  | DE | ODE |  | Full |  |  | 75% | 3/4 Load | 1/2 Load |  |  | 3/4 Load |  |  | Eff'y | Eff'y | Eff'y | Eff'y | Eff'y | P.F. | P.F. | P.F. | TIME | TIME | Motor | Max | SOUND | FL | 3/4 Load | (Starts per HR) |  | BTWN | Max. | Toshiba | NEMA | Rotor |  |  | Rise | Rise | of | Speed | Torque
HP: | RPM: | Bearing | Bearing | Frame | Load | Idle | FLC | Current | Current | Current | LRC | FLT | Torque | LRT | BDT | @1.0 | @1.0 | @0.75 | @0.75 | @O.5 | @ 1.0 | @.75 | @0.5 | COLD | HOT | Inrush | KVAR | LEVELS | Watts | Watts | Cold | Hot | STARTS | WK2 | WK2 | WK2 | Inertia | Weight | Ins. | @1.0 | @1.15 | Conn. | @FLT | @ 10Hz
|  |  |  | (#) | RPM | (A) | (A) | (A) | (A) | (A) | (A) | (lbft) | (lbft) | (%) | (%) | (%) | (%) | (%) | (%) | (%) | (%) | (%) | (%) | (Sec) | (Sec) | (A) |  |  | Loss | Loss | (Sec) | (Sec) | (Sec) | (lbft2) | (lbft2) | (lbft2) | (lbft2) | (Lbs) | (Cl) | (Deg) | (Deg) | (Y / D) | (Hz) | (%)
[24 empty] | ** | ** | [17 empty] | *** | ***
0.75 | 900 | 6205ZZ | 6205ZZ | 145T | 860 | 1.6 | 2 | 1.9 |  |  | 8 | 4.6 | 3.4 | 240 | 250 | 70 | 66.0377 | 67.2 | 63.1 | 61.8 | 49 | 40.8 | 30.7 | 51 | 21 | 26 |  | 48 | 239.7857 | 204.817 |  |  |  | 198 | 198 |  | TBA | 57 | F | 55 | 65 | Y | CF | CF
0.75 | 1200 | 6305UUC3 | 6305UUC3 | 143T | 1160 | 1.1 | 1.4 | 1.3 |  |  | 9.5 | 3.4 | 2.5 | 365 | 375 | 79.8 | 76.7013 | 78.7 | 75.5 | 74.8 | 61.5 | 52 | 40.7 | 52 | 30 | 18.2 | 0.8 | 50 | 141.6278 | 113.5707 | 35 | 34 |  | 87 | 113.1 |  | 0.1144 | 46 | F | 23 | 29 | Y | 10 | 100
0.75 | 1800 | 6305UUC3 | 6305UUC3 | 143T | 1762 | 0.8 | 1.1 | 1.1 |  |  | 11 | 2.2 | 1.7 | 448 | 491 | 84.7 | 82.1851 | 82.9 | 80.2 | 81.3 | 72.7 | 60.2 | 52.7 | 44 | 26 | 14.3 | 0.5 | 46 | 101.0667 | 86.5571 | 31 | 30 |  |  |  |  | 0.11245 | 42 | F | 14 | 17 | Y | 10 | 100
0.75 | 3600 | 6305UUC3 | 6305UUC3 | 143T | 3545 | 1.1 | 1.4 | 1.2 |  |  | 20 | 1.1 | 0.8 | 700 | 800 | 80.5 | 77.4783 | 79 | 75.8 | 75.3 | 63.2 | 53.5 | 47.6 | 34 | 20 | 18.2 | 0.8 | 58 | 135.5311 | 111.5459 | 16 | 15 |  |  |  |  | 0.06565 | 53 | F | 19 | 23 | Y | 10 | 100
1 | 900 | 6207ZZ | 6205ZZ | 182T | 862 | 1.8 | 2.1 | 1.8 |  |  | 9.75 | 6.1 | 4.5 | 202 | 306 | 74 | 70.3422 | 76.1 | 72.6 | 71.5 | 60 | 51 | 39.9 | 51 | 21 | 27.3 |  | 48 | 262.1081 | 175.7168 |  |  |  | 308 | 308 | 31 | TBA | 82 | F | 40 | 52 | Y | CF | CF
1 | 1200 | 6305UUC3 | 6305UUC3 | 145T | 1152 | 1.3 | 1.8 | 1.6 |  |  | 12 | 4.6 | 3.4 | 285 | 320 | 82.4 | 79.5981 | 82 | 79.2 | 78 | 63 | 54.5 | 40.9 | 52 | 28 | 23.4 | 0.6 | 50 | 159.3398 | 122.8171 | 35 | 34 | 33 | 93 | 120.9 | 15 | 0.1365 | 49 | F | 40 | 46 | Y | 10 | 100
1 | 1800 | 6305UUC3 | 6305UUC3 | 143T | 1749 | 0.8 | 1.4 | 1.1 |  |  | 11 | 3 | 2.2 | 336 | 368 | 85.7 | 83.3171 | 86.1 | 83.8 | 84.1 | 79.1 | 72.7 | 59.8 | 36 | 24 | 18.2 | 0.5 | 46 | 124.4784 | 90.3258 | 31 | 30 | 38 | 37 | 48.1 | 5.8 | 0.11245 | 43 | F | 18 | 21 | Y | 10 | 100
1 | 3600 | 6305UUC3 | 6305UUC3 | 143T | 3526 | 1.1 | 1.5 | 1.4 |  |  | 20 | 1.5 | 1.1 | 525 | 600 | 83.3 | 80.6077 | 80.5 | 77.5 | 78.8 | 74.5 | 63.3 | 51.1 | 34 | 20 | 19.5 | 0.8 | 58 | 149.5582 | 135.5311 | 16 | 15 | 75 |  |  |  | 0.06565 | 53 | F | 23 | 29 | Y | 10 | 100
1.5 | 900 | 6207ZZ | 6205ZZ | 184T | 866 | 2.3 | 3 | 2.7 |  |  | 15 | 9.1 | 6.8 | 206 | 299 | 77 | 73.6138 | 76 | 72.5 | 71.4 | 60.4 | 51.4 | 40.3 | 51 | 21 | 39 |  | 46 | 334.2468 | 265.0263 |  |  |  | 340 | 340 | 45 | TBA | 90 | F | 40 | 52 | Y | CF | CF
1.5 | 1200 | 6306UUC3 | 6306UUC3 | 182T | 1168 | 1.5 | 2.4 | 2 |  |  | 20 | 6.7 | 5 | 266 | 398 | 86.4 | 84.1121 | 86.1 | 83.8 | 84.1 | 68.2 | 60.3 | 46.9 | 50 | 26 | 31.2 | 1.2 | 49 | 176.1389 | 135.4887 | 30 | 29 | 34 | 149 | 193.7 | 23 | 0.2912 | 77 | F | 25 | 41 | Y | 10 | 100
1.5 | 1800 | 6305UUC3 | 6305UUC3 | 145T | 1740 | 1.1 | 2.1 | 1.7 |  |  | 20 | 4.5 | 3.4 | 385 | 370 | 86.9 | 84.6813 | 87.1 | 84.9 | 85.7 | 78.7 | 71.1 | 59.2 | 34 | 22 | 27.3 | 0.8 | 46 | 168.687 | 124.2976 | 27 | 26 | 38 | 47 | 61.1 | 8.6 | 0.1495 | 49 | F | 37 | 46 | Y | 10 | 100
1.5 | 3600 | 6305UUC3 | 6305UUC3 | 143T | 3489 | 1.1 | 2 | 1.7 |  |  | 20 | 2.3 | 1.7 | 350 | 400 | 85.4 | 82.9771 | 84.9 | 82.4 | 82.4 | 81.9 | 75.1 | 63.2 | 34 | 20 | 26 | 0.8 | 57 | 191.3044 | 149.2659 | 13 | 12 | 76 | 9.3 | 12.09 | 1.8 | 0.06565 | 53 | F | 28 | 35 | Y | 10 | 100
2 | 900 | 6308UU | 6208UU | 213T | 863 | 2.3 | 3.5 | 3 |  |  | 16.1 | 12.2 | 9 | 165 | 257 | 80 | 76.9231 | 80.2 | 77.1 | 77.4 | 67.4 | 59.2 | 46.6 | 46 | 19 | 45.5 |  | 48 | 373 | 276.2618 |  |  |  | 455 | 455 | 60 | TBA | 137 | F | 45 | 57 | Y | CF | CF
2 | 1200 | 6306UUC3 | 6306UUC3 | 184T | 1172 | 2 | 3.2 | 2.8 |  |  | 25 | 9 | 6.7 | 280 | 376 | 88.4 | 86.3956 | 87.7 | 85.6 | 85.3 | 66.7 | 58.1 | 45.6 | 50 | 24 | 41.6 | 1.6 | 50 | 195.7828 | 156.9407 | 27 | 26 | 35 | 167 | 217.1 | 30 | 0.3536 | 86 | F | 23 | 31 | Y | 10 | 100
2 | 1800 | 6305UUC3 | 6305UUC3 | 145T | 1733 | 1.4 | 2.7 | 2.2 |  |  | 25 | 6.1 | 4.5 | 380 | 340 | 86.8 | 84.5674 | 87.3 | 85.1 | 86.2 | 80.4 | 73.3 | 61.6 | 34 | 20 | 35.1 | 1.1 | 52 | 226.894 | 162.7869 | 24 | 23 | 39 | 56 | 72.8 | 11 | 0.1729 | 54 | F | 34 | 38 | Y | 10 | 100
2 | 3600 | 6305UUC3 | 6305UUC3 | 145T | 3499 | 1.3 | 2.6 | 2.1 |  |  | 25 | 3 | 2.2 | 350 | 400 | 86.4 | 84.1121 | 86.3 | 84 | 84.4 | 84.1 | 77.7 | 65.8 | 31 | 18 | 33.8 | 1 | 58 | 234.8519 | 177.6396 | 13 | 12 | 77 | 10.6 | 13.78 | 2.4 | 0.07735 | 53 | F | 33 | 39 | Y | 10 | 100
3 | 900 | 6308UU | 6208UU | 215T | 864 | 3.5 | 5.2 | 4.4 |  |  | 26 | 18.2 | 13.5 | 200 | 265 | 82.5 | 79.7101 | 82 | 79.2 | 79.2 | 65.6 | 58.6 | 46.7 | 41 | 15 | 67.6 |  | 49 | 474.7273 | 368.4512 |  |  |  | 553 | 553 | 87 | TBA | 161 | F | 53 | 65 | Y | CF | CF
3 | 1200 | 6308C3 | 6308C3 | 213T | 1167 | 2.1 | 4 | 3.3 |  |  | 32 | 13.5 | 10.1 | 279 | 352 | 90.3 | 88.5815 | 91 | 89.4 | 89.9 | 78 | 70 | 57.7 | 48 | 20 | 52 | 1.6 | 50 | 240.4053 | 166.0055 | 24 | 23 | 36 | 260 | 338 | 44 | 0.65 | 125 | F | 22 | 27 | Y | 10 | 100
3 | 1800 | 6306UUC3 | 6306UUC3 | 182T | 1754 | 1.5 | 3.7 | 3 |  |  | 32 | 9 | 6.7 | 259 | 373 | 89.5 | 87.6592 | 89.7 | 87.9 | 88.6 | 84.2 | 79 | 68.2 | 28 | 15 | 48.1 | 1.2 | 54 | 262.5587 | 192.7375 | 21 | 20 | 40 | 81 | 105.3 | 17 | 0.3185 | 77 | F | 34 | 41 | Y | 10 | 100
3 | 3600 | 6306UUC3 | 6306UUC3 | 182T | 3509 | 1.1 | 3.5 | 2.7 |  |  | 32 | 4.5 | 3.3 | 248 | 388 | 88.8 | 86.8545 | 88.9 | 87 | 87.6 | 91.1 | 87.9 | 81 | 24 | 12 | 45.5 | 0.8 | 59 | 282.2703 | 209.5765 | 11 | 10 | 80 | 18.6 | 24.18 | 3.5 | 0.11115 | 77 | F | 25 | 30 | Y | 10 | 100
5 | 900 | 6309UU | 6208UU | 254T | 874 | 3.9 | 7.6 | 6.2 |  |  | 34 | 30 | 22.4 | 156 | 214 | 86.5 | 84.2259 | 87.3 | 85.1 | 86 | 70.9 | 65.2 | 54.8 | 31 | 11 | 98.8 |  | 49 | 582.1387 | 406.9674 |  |  |  | 985 | 985 | 142 | TBA | 240 | F | 47 | 59 | Y | CF | CF
5 | 1200 | 6308C3 | 6308C3 | 215T | 1165 | 3.1 | 6.5 | 5.4 |  |  | 46 | 22.5 | 16.8 | 279 | 376 | 90.1 | 88.3507 | 89.7 | 87.9 | 87.4 | 79.4 | 72.7 | 60.6 | 48 | 18 | 84.5 | 4.9 | 49 | 409.8446 | 321.2291 | 20 | 19 | 37 | 305 | 396.5 | 71 | 0.9555 | 153 | F | 32 | 41 | Y | 10 | 100
5 | 1800 | 6306UUC3 | 6306UUC3 | 184T | 1737 | 2.1 | 6.1 | 4.7 | 4.7 | 3.5 | 46 | 15.1 | 11.2 | 265 | 290 | 88.4 | 86.3956 | 89.7 | 87.9 | 89.4 | 86.7 | 83.6 | 75.5 | 28 | 13 | 79.3 | 1.7 | 55 | 489.457 | 321.2291 | 17 | 16 | 42 | 99 | 128.7 | 27 | 0.4329 | 101 | F | 56 | 79 | Y | 30 | 90
5 | 3600 | 6306UUC3 | 6306UUC3 | 184T | 3502 | 1.5 | 5.7 | 4.4 |  |  | 46 | 7.5 | 5.6 | 265 | 357 | 89 | 87.0841 | 89.1 | 87.2 | 87.7 | 92.5 | 90.4 | 84.8 | 24 | 12 | 74.1 | 1.2 | 60 | 461.0112 | 342.2306 | 9 | 8 | 83 | 25.2 | 32.76 | 5.7 | 0.1924 | 99 | F | 45 | 56 | Y | 10 | 100
7.5 | 900 | 6309UU | 6208UU | 256T | 878 | 6.4 | 11.7 | 9.7 |  |  | 59 | 44.8 | 33.4 | 170 | 244 | 87.5 | 85.3659 | 88 | 85.9 | 87.3 | 68.4 | 61.9 | 50.7 | 37 | 12 | 152.1 |  | 50 | 799.2857 | 572.2159 |  |  |  | 1050 | 1050 | 208 | TBA | 299 | F | 37 | 46 | D | CF | CF
7.5 | 1200 | 6309C3 | 6308C3 | 254T | 1179 | 4.5 | 9.7 | 7.8 |  |  | 63.5 | 33.4 | 24.9 | 218 | 340 | 92 | 90.5512 | 91.8 | 91.1 | 90.6 | 78.6 | 73.2 | 62.7 | 48 | 20 | 126.1 | 3.5 | 51 | 486.5217 | 374.8284 | 17 | 16 | 39 | 640 | 832 | 104 | 2.314 | 222 | F | 31 | 38 | D | 10 | 100
7.5 | 1800 | 6308C3 | 6308C3 | 213T | 1752 | 3.6 | 9.2 | 7.3 |  |  | 63.5 | 22.5 | 16.7 | 280 | 290 | 90.9 | 89.2752 | 91.2 | 90.4 | 90.3 | 84 | 79 | 69 | 24 | 12 | 119.6 | 2.8 | 57 | 560.1155 | 404.9013 | 15 | 14 | 44 | 155 | 201.5 | 39 | 1.0205 | 153 | F | 43 | 60 | D | 20 | 90
7.5 | 3600 | 6308C3 | 6308ZC3 | 213T | 3515 | 2.5 | 8.8 | 6.8 |  |  | 63.5 | 11.2 | 8.4 | 213 | 310 | 90.5 | 88.8126 | 90.3 | 89.4 | 89 | 88.5 | 85.8 | 79 | 24 | 12 | 114.4 | 2 | 62 | 587.3204 | 450.76 | 8 | 7 | 88 | 29.6 | 38.48 | 8.3 | 0.5109 | 165 | F | 48 | 60 | D | 10 | 100
10 | 900 | 6310C3 | 6310CZZ3 | 284T | 879 | 8.3 | 15.3 | 12.6 |  |  | 80 | 59.7 | 44.5 | 205 | 244 | 88.5 | 86.5103 | 89.1 | 87.2 | 87.5 | 69.2 | 62.5 | 51.1 | 35 | 11 | 198.9 |  | 50 | 969.3785 | 684.4613 |  |  |  | 1700 | 1700 | 273 | TBA | 416 | F | 32 | 39 | D | CF | CF
10 | 1200 | 6309C3 | 6308C3 | 256T | 1176 | 5.3 | 12.8 | 10.1 |  |  | 63.5 | 44.6 | 33.3 | 234 | 283 | 92.5 | 91.133 | 92.8 | 92.1 | 92 | 79.2 | 74.7 | 64.8 | 48 | 18 | 166.4 | 4.1 | 52 | 604.8649 | 434.0948 | 16 | 15 | 41 | 675 | 877.5 | 137 | 2.613 | 251 | F | 38 | 49 | D | 10 | 100
10 | 1800 | 6308C3 | 6308C3 | 215T | 1746 | 4 | 11.9 | 9.4 |  |  | 81 | 30.1 | 22.4 | 290 | 295 | 90.9 | 89.2752 | 91.3 | 90.5 | 90.4 | 86.5 | 82 | 73 | 22 | 10 | 154.7 | 3.2 | 55 | 746.8207 | 533.149 | 14 | 13 | 46 | 163 | 211.9 | 51 | 1.1375 | 168 | F | 47 | 64 | D | 20 | 90
10 | 3600 | 6308C3 | 6308C3 | 215T | 3510 | 2.9 | 11.6 | 8.9 |  |  | 81 | 15 | 11.1 | 212 | 300 | 90.3 | 88.5815 | 90 | 89.1 | 88 | 89.7 | 87.6 | 81.7 | 22 | 10 | 150.8 | 2.3 | 62 | 801.3511 | 621.6667 | 7 | 6 | 92 | 37.5 | 48.75 | 11 | 0.7046 | 196 | F | 59 | 74 | D | 60 | 80
15 | 900 | 6310C3 | 6310CZZ3 | 286T | 877 | 12 | 22.4 | 18.5 |  |  | 99 | 89.8 | 66.9 | 214 | 226 | 89.5 | 88.57 | 89.3 | 87.4 | 87.9 | 70 | 63.6 | 52.6 | 39 | 14 | 291.2 |  | 55 | 1312.7933 | 1005.5963 |  |  |  | 1880 | 1880 | 400 | TBA | 404 | F | 47 | 61 | D | CF | CF
15 | 1200 | 6310C3 | 6310C3 | 284T | 1173 | 7.1 | 18.6 | 14.7 |  |  | 116 | 67.1 | 50.1 | 208 | 277 | 92.3 | 91.5947 | 92.5 | 91.8 | 92 | 82 | 77.7 | 68.3 | 45 | 18 | 241.8 | 5.6 | 59 | 933.5103 | 680.473 | 13 | 12 | 44 | 1120 | 1456 | 200 | 5.2 | 374 | F | 45 | 58 | D | 30 | 85
15 | 1800 | 6309C3 | 6308C3 | 254T | 1774 | 6.6 | 18.2 | 14.3 |  |  | 110 | 44.4 | 33.2 | 229 | 254 | 92.4 | 91.7031 | 92.6 | 91.9 | 91.8 | 83.6 | 79.7 | 71 | 24 | 12 | 236.6 | 5.2 | 61 | 920.3896 | 670.6749 | 12 | 11 | 50 | 296 | 384.8 | 75 | 2.106 | 234 | F | 45 | 56 | D | 10 | 100
15 | 3600 | 6309C3 | 6308C3 | 254T | 3533 | 3.4 | 16.7 | 12.5 |  |  | 116 | 22.3 | 16.6 | 220 | 290 | 91.6 | 91 | 92 | 91.3 | 91.6 | 91.9 | 91.8 | 91.1 | 24 | 11 | 217.1 | 2.7 | 65 | 1026.1572 | 729.7826 | 7 | 6 | 100 | 40 | 52 | 16 | 1.378 | 266 | F | 56 | 75 | D | 30 | 90
20 | 900 | 6312C3 | 6312ZZC3 | 324T | 879 | 13.8 | 29.6 | 23.8 |  |  | 142.5 | 119 | 89.1 | 225 | 204 | 89.5 | 88.57 | 89.9 | 88.1 | 88.9 | 70.8 | 65.7 | 55.4 | 28 | 12 | 384.8 |  | 55 | 1750.3911 | 1257.1635 |  |  |  | 2580 | 2580 | 525 | TBA | 591 | F | 48 | 62 | D | CF | CF
20 | 1200 | 6310C3 | 6310C3 | 286T | 1170 | 10 | 24.3 | 18.9 | 18.9 | 14.1 | 145 | 89.7 | 66.9 | 205 | 275 | 92.3 | 91.5947 | 92.6 | 91.9 | 92.2 | 83.5 | 80.2 | 72.2 | 44 | 16 | 315.9 | 7.9 | 59 | 1244.6804 | 894.2333 | 12 | 11 | 48 | 1250 | 1625 | 262 | 6.37 | 404 | F | 50 | 66 | D | 30 | 85
20 | 1800 | 6309C3 | 6308C3 | 256T | 1772 | 8.1 | 23.7 | 18.5 |  |  | 145 | 59.3 | 44.3 | 225 | 240 | 93.1 | 92.462 | 93.4 | 92.8 | 93 | 84.9 | 81.4 | 73.3 | 21 | 9 | 308.1 | 6.4 | 61 | 1105.7787 | 790.7281 | 11 | 10 | 55 | 344 | 447.2 | 99 | 2.873 | 285 | F | 51 | 66 | D | 20 | 90
20 | 3600 | 6309C3 | 6308C3 | 256T | 3535 | 4.125 | 21.8 | 16.3 |  |  | 145 | 29.7 | 22.2 | 250 | 280 | 92.5 | 91.8114 | 93.2 | 92.6 | 93.2 | 92.9 | 92.3 | 88.9 | 21 | 9 | 283.4 | 3.3 | 72 | 1209.7297 | 816.4378 | 6 | 5 | 110 | 50.6 | 65.78 | 21 | 2.08 | 312 | F | 56 | 80 | D | 60 | 80
25 | 900 | 6312C3 | 6312ZZC3 | 326T | 881 | 18.3 | 35.9 | 29.3 |  |  | 182.5 | 149 | 111 | 250 | 236 | 91 | 90.1883 | 90.9 | 89.3 | 88.7 | 71.6 | 66 | 55.3 | 30 | 10 | 466.7 |  | 59 | 1844.5055 | 1400.2888 |  |  |  | 2770 | 2770 | 647 | TBA | 683 | F | 59 | 73 | D | CF | CF
25 | 1200 | 6312C3 | 6312C3 | 324T | 1175 | 12.5 | 31.1 | 24.4 |  |  | 182.5 | 112 | 83.3 | 245 | 255 | 92.9 | 92.2451 | 93.5 | 92.9 | 93 | 80.9 | 76.8 | 67.7 | 42 | 20 | 404.3 | 9.9 | 59 | 1425.3498 | 972.393 | 11 | 10 | 51 | 1730 | 2249 | 324 | 8.45 | 496 | F | 46 | 61 | D | 10 | 100
25 | 1800 | 6310C3 | 6310C3 | 284T | 1770 | 10.5 | 29.3 | 22.7 |  |  | 182.5 | 74.2 | 55.4 | 240 | 260 | 93.5 | 92.8962 | 93.7 | 93.1 | 93.1 | 85.5 | 82.6 | 75 | 21 | 8 | 380.9 | 8.3 | 67 | 1296.5241 | 940.4616 | 10 | 9 | 58 | 400 | 520 | 122 | 3.12 | 370 | F | 51 | 67 | D | 30 | 90
25 | 3600 | 6310C3 | 6310C3 | 284TS | 3529 | 5 | 27.2 | 20.4 |  |  | 182.5 | 37.2 | 27.8 | 260 | 250 | 92.4 | 91.7031 | 93 | 92.4 | 92 | 93.2 | 92.4 | 89.6 | 21 | 8 | 353.6 | 4 | 81 | 1533.9827 | 1052.8226 | 6 | 5 | 115 | 106 | 137.8 | 26 | 3.25 | 411 | F | 53 | 75 | D | 60 | 80
30 | 900 | 6314C3 | 6312C3 | 364T | 879 | 20.4 | 41.6 | 33.6 |  |  | 217.5 | 179 | 134 | 252 | 203 | 91 | 90.1883 | 91 | 89.4 | 89.5 | 74.2 | 69 | 58.4 | 29 | 10 | 540.8 |  | 59 | 2213.4066 | 1660.0549 |  |  |  | 2900 | 2900 | 769 | TBA | 816 | F | 53 | 67 | D | CF | CF
30 | 1200 | 6312C3 | 6312C3 | 326T | 1177 | 14 | 37 | 29 |  |  | 217.5 | 134 | 100 | 245 | 254 | 93.6 | 93.0048 | 94 | 93.4 | 93.7 | 81.2 | 77.2 | 68.1 | 42 | 18 | 481 | 11.1 | 61 | 1530.2564 | 1071.383 | 10 | 9 | 53 | 1840 | 2392 | 384 | 10.01 | 539 | F | 49 | 63 | D | 20 | 90
30 | 1800 | 6310C3 | 6310C3 | 286T | 1770 | 13 | 35.1 | 27.2 |  |  | 217.5 | 89 | 66.5 | 255 | 275 | 93.4 | 93 | 93.6 | 93 | 93 | 85.7 | 82.7 | 75.6 | 20 | 7 | 456.3 | 10.3 | 69 | 1581.4561 | 1147.6923 | 9 | 8 | 60 | 443 | 575.9 | 144 | 4.03 | 404 | F | 63 | 81 | D | 60 | 80
30 | 3600 | 6310C3 | 6310C3 | 286TS | 3524 | 6 | 32.5 | 24.4 |  |  | 217.5 | 44.7 | 33.3 | 260 | 250 | 92.4 | 91.7031 | 93.1 | 92.5 | 92.1 | 93.5 | 92.8 | 90.5 | 20 | 7 | 422.5 | 4.7 | 82 | 1840.7792 | 1244.0011 | 5 | 4 | 120 | 112 | 145.6 | 31 | 3.51 | 462 | F | 58 | 75 | D | 60 | 80
40 | 900 | 6314C3 | 6312C3 | 365T | 877 | 24.5 | 54 | 42.8 |  |  | 272.5 | 239 | 178 | 220 | 213 | 91 | 90.1883 | 91.7 | 90.2 | 91.3 | 76.2 | 71.5 | 61.6 | 29 | 11 | 702 |  | 60 | 2951.2088 | 2025.6707 |  |  |  | 3170 | 3170 | 1007 | TBA | 920 | F | 50 | 64 | D | CF | CF
40 | 1200 | 6314C3 | 6312C3 | 364T | 1176 | 14.5 | 46.9 | 36.1 |  |  | 290 | 179 | 133 | 245 | 260 | 94 | 93.6 | 94.6 | 94.1 | 94.5 | 84.9 | 82.2 | 74.8 | 40 | 20 | 609.7 | 11.6 | 66 | 1904.6809 | 1277.5053 | 10 | 9 | 57 | 1900 | 2470 | 503 | 17.68 | 714 | F | 51 | 69 | D | 30 | 85
40 | 1800 | 6312C3 | 6312C3 | 324T | 1770 | 16 | 47.9 | 37 |  |  | 290 | 119 | 88.6 | 250 | 260 | 94 | 93.6 | 94.4 | 93.9 | 94.1 | 83.2 | 80.4 | 72.9 | 25 | 11 | 622.7 | 12.7 | 71 | 1904.6809 | 1327.6271 | 9 | 8 | 65 | 593 | 770.9 | 189 | 8.45 | 568 | F | 54 | 67 | D | 30 | 80
40 | 3600 | 6312C3 | 6312C3 | 324TS | 3535 | 11 | 44.8 | 33.7 |  |  | 290 | 59.4 | 44.4 | 260 | 240 | 93.1 | 92.462 | 93.4 | 92.8 | 92.8 | 89.7 | 89.2 | 84.3 | 28 | 11 | 582.4 | 8.7 | 80 | 2211.5575 | 1581.4561 | 5 | 4 | 130 | 137 | 178.1 | 40 | 5.33 | 574 | F | 63 | 87 | D | 40 | 85
50 | 900 | 6317C3 | 6313C3 | 404T | 879 | 20 | 62 | 47 |  |  | 352.5 | 299 | 223 | 150 | 225 | 91 | 90.1883 | 92 | 90.6 | 91.3 | 83 | 81.2 | 74.6 | 29 | 11 | 806 |  | 66 | 3689.011 | 2432.6087 |  |  |  | 4300 | 4300 | 1241 | TBA | 1150 | F | 55 | 74 | D | CF | CF
50 | 1200 | 6314C3 | 6312C3 | 365T | 1175 | 18.5 | 59.9 | 46.6 |  |  | 362.5 | 223 | 167 | 250 | 264 | 93.6 | 93.6 | 94.4 | 93.9 | 94.3 | 83.5 | 79.9 | 71 | 40 | 18 | 778.7 | 14.7 | 67 | 2550.4274 | 1659.5339 | 9 | 8 | 64 | 2090 | 2717 | 620 | 22.36 | 793 | F | 63 | 83 | D | 30 | 80
50 | 1800 | 6312C3 | 6312C3 | 326T | 1771 | 20 | 59.2 | 45.8 |  |  | 362.5 | 148 | 111 | 260 | 240 | 94 | 93.6 | 94.2 | 93.7 | 93.9 | 84.2 | 81.4 | 74.5 | 22 | 10 | 769.6 | 16 | 71 | 2380.8511 | 1722.4522 | 8 | 7 | 72 | 625 | 812.5 | 232 | 9.23 | 595 | F | 51 | 67 | D | 30 | 80
50 | 3600 | 6312C3 | 6312C3 | 326TS | 3533 | 12 | 55.4 | 42 |  |  | 362.5 | 74.3 | 55.5 | 270 | 270 | 93 | 92.3535 | 93.3 | 92.7 | 92.6 | 90.9 | 89.7 | 86 | 23 | 10 | 720.2 | 9.5 | 81 | 2807.5269 | 2008.9228 | 5 | 4 | 145 | 156 | 202.8 | 49 | 6.37 | 690 | F | 67 | 90 | D | 60 | 75
60 | 900 | 6317C3 | 6313C3 | 405T | 880 | 27 | 76 | 59.3 |  |  | 430 | 358 | 267 | 190 | 230 | 91 | 90.1883 | 91.3 | 89.7 | 91.3 | 81.2 | 77.8 | 69.9 | 29 | 10 | 988 |  | 68 | 4426.8132 | 3198.8938 |  |  |  | 4600 | 4600 | 1473 | TBA | 1495 | F | 65 | 90 | D | CF | CF
60 | 1200 | 6317C3 | 6313C3 | 404T | 1187 | 26 | 72.7 | 57.2 |  |  | 435 | 265 | 198 | 210 | 244 | 95 | 94.5274 | 95.1 | 94.6 | 94.6 | 81.4 | 77.5 | 69.5 | 38 | 20 | 945.1 | 20.7 | 70 | 2355.7895 | 1729.6845 | 8 | 7 | 75 | 2630 | 3419 | 735 | 31.59 | 1144 | F | 58 | 70 | D | 30 | 90
60 | 1800 | 6314C3 | 6312C3 | 364T | 1777 | 22 | 70.3 | 54.3 |  |  | 435 | 177 | 133 | 216 | 274 | 95.1 | 94.6363 | 95.2 | 94.7 | 94.6 | 84 | 81.5 | 74.9 | 21 | 8 | 913.9 | 17.5 | 72 | 2306.2461 | 1692.605 | 7 | 6 | 85 | 770 | 1001 | 275 | 13.91 | 741 | F | 51 | 62 | D | 60 | 50
60 | 3600 | 6312C3 | 6312C3 | 364TS | 3547 | 18.5 | 67.3 | 51.2 |  |  | 435 | 88.8 | 66.4 | 230 | 280 | 93.8 | 93.222 | 94 | 93.4 | 93.7 | 89 | 87.5 | 82.6 | 29 | 10 | 874.9 | 14.7 | 85 | 2958.5501 | 2142.766 | 4 | 3 | 170 | 169 | 219.7 | 58 | 10.01 | 845 | F | 63 | 85 | D | 40 | 80
75 | 900 | NU318C3 | 6318C3 | 444T | 882 | 33 | 95.5 | 74 |  |  | 540 | 446 | 333 | 175 | 250 | 91.7 | 90.9452 | 92.3 | 90.9 | 92 | 80.2 | 77.1 | 68.2 | 29 | 10 | 1241.5 |  | 69 | 5064.1767 | 3500.6636 |  |  |  | 6170 | 6170 | 1814 | TBA | 1932 | F | 71 | 98 | D | CF | CF
75 | 1200 | 6317C3 | 6313C3 | 405T | 1186 | 32 | 90.7 | 70.6 |  |  | 542.5 | 332 | 248 | 210 | 241 | 94.9 | 94.4185 | 95.1 | 94.6 | 94.5 | 81.6 | 78.4 | 69.6 | 28 | 15 | 1179.1 | 25.5 | 70 | 3006.7966 | 2162.1057 | 8 | 7 | 79 | 2930 | 3809 | 904 | 62.53 | 1292 | F | 46 | 60 | D | 30 | 90
75 | 1800 | 6314C3 | 6312C3 | 365T | 1775 | 29 | 87.9 | 68.3 |  |  | 542.5 | 222 | 166 | 200 | 270 | 95.3 | 94.8542 | 95.5 | 95.1 | 95 | 83.8 | 80.8 | 73.9 | 20 | 7 | 1142.7 | 23.1 | 79 | 2759.3389 | 1977.2906 | 7 | 6 | 90 | 862 | 1120.6 | 338 | 17.68 | 853 | F | 58 | 74 | D | 60 | 30
75 | 3600 | 6312C3 | 6312C3 | 365TS | 3540 | 22 | 84.9 | 64.5 |  |  | 542.5 | 111 | 83.1 | 260 | 270 | 93.5 | 92.8962 | 93.8 | 93.2 | 93.4 | 88.5 | 87 | 82 | 21 | 8 | 1103.7 | 17.5 | 85 | 3889.5722 | 2773.6407 | 4 | 3 | 180 | 194 | 252.2 | 71 | 11.57 | 908 | F | 60 | 80 | D | 60 | 80
100 | 900 | NU318C3 | 6318C3 | 445T | 881 | 38 | 122 | 95 |  |  | 720 | 596 | 445 | 190 | 240 | 92.4 | 91.7031 | 93 | 91.7 | 92.8 | 83.2 | 79.5 | 73.1 | 27 | 9 | 1586 |  | 69 | 6135.9307 | 4211.2903 |  |  |  | 7080 | 7080 | 2372 | 85.4 | 2291 | F | 71 | 98 | D | CF | CF
100 | 1200 | NU318C3 | 6318C3 | 444T | 1183 | 41 | 122 | 94.3 |  |  | 725 | 444 | 332 | 200 | 225 | 95.5 | 95.0722 | 95.7 | 95.3 | 95.2 | 80.1 | 77.8 | 69.8 | 18 | 9 | 1586 | 32.6 | 76 | 3515.1832 | 2513.9498 | 7 | 6 | 97 | 3300 | 4290 | 1181 | 57.85 | 1764 | F | 62 | 81 | D | 60 | 85
100 | 1800 | 6317C3 | 6313C3 | 405T | 1776 | 37 | 117 | 90.5 |  |  | 725 | 296 | 221 | 200 | 256 | 95.4 | 94.9632 | 95.6 | 95.2 | 95.3 | 84.1 | 81.2 | 74.3 | 19 | 9 | 1521 | 29.5 | 79 | 3597.065 | 2575.1046 | 6 | 5 | 110 | 1062 | 1380.6 | 441 | 28.47 | 1324 | F | 69 | 87 | D | 60 | 80
100 | 3600 | 6313C3 | 6313C3 | 405TS | 3557 | 26.5 | 112 | 85.8 |  |  | 725 | 148 | 110 | 215 | 260 | 95 | 94.5274 | 95 | 94.5 | 94.8 | 87.8 | 86.2 | 81 | 20 | 10 | 1456 | 21.1 | 85 | 3926.3158 | 2944.7368 | 4 | 3 | 220 | 262 | 340.6 | 92 | 20.02 | 1357 | F | 67 | 89 | D | 60 | 75
125 | 900 | NU322C3 | 6318C3 | 505UZ | 885 | 52.5 | 156 | 121 |  |  | 815 | 742 | 554 | 125 | 220 | 93.6 | 93.0048 | 93.8 | 92.7 | 93.3 | 80.2 | 77.3 | 69.7 | 30 | 12 | 2028 |  | 69 | 6376.0684 | 4622.7345 |  |  |  | 7900 | 7900 | 2919 | 80.7 | 2943 | F | 64 | 83 | D | CF | CF
125 | 1200 | NU318C3 | 6318C3 | 445T | 1186 | 64 | 155 | 119 |  |  | 907.5 | 553 | 414 | 206 | 230 | 95.5 | 95.0722 | 95.6 | 95.2 | 95.5 | 79.1 | 77 | 69 | 15 | 8 | 2015 | 51 | 74 | 4393.9791 | 3218.8808 | 7 | 6 | 120 | 3560 | 4628 | 1452 | 66.43 | 1919 | F | 67 | 88 | D | 60 | 85
125 | 1800 | NU318C3 | 6318C3 | 444T | 1785 | 46 | 145 | 113 |  |  | 907.5 | 368 | 275 | 216 | 256 | 95.7 | 95.2903 | 95.7 | 95.3 | 95 | 84.1 | 81.1 | 73.3 | 18 | 11 | 1885 | 36.6 | 84 | 4189.9164 | 3142.4373 | 6 | 5 | 140 | 1490 | 1937 | 542 | 44.72 | 1762 | F | 61 | 79 | D | 60 | 70
125 | 3600 | 6313C3 | 6313C3 | 444TS | 3575 | 36.5 | 139 | 105 |  |  | 907.5 | 184 | 137 | 215 | 265 | 95.3 | 94.8542 | 95.2 | 94.7 | 94.8 | 88.2 | 87.5 | 84.3 | 19 | 10 | 1807 | 29 | 85 | 4598.8982 | 3526.2605 | 4 | 3 | 275 | 430 | 559 | 113 | 36.27 | 1873 | F | 62 | 75 | D | 30 | 85
150 | 900 | NU322C3 | 6318C3 | 505UZ | 884 | 66.25 | 187 | 144 |  |  | 1035 | 891 | 665 | 130 | 225 | 93.6 | 93.0048 | 93.7 | 92.5 | 93.5 | 80.2 | 78.1 | 69.5 | 33 | 14 | 2431 |  | 71 | 7651.2821 | 5642.7695 |  |  |  | 10200 | 10200 | 3456 | 92 | 4213 | F | 68 | 88 | D | CF | CF
150 | 1200 | NU318C3 | 6318C3 | 447T | 1184 | 65 | 181 | 141 |  |  | 1085 | 665 | 497 | 220 | 245 | 95.8 | 95.3993 | 96.2 | 95.8 | 96.1 | 81.1 | 77.7 | 68.7 | 13 | 7 | 2353 | 51.7 | 77 | 4905.8455 | 3315.1247 | 6 | 5 | 140 | 3800 | 4940 | 1719 | 76.31 | 2132 | F | 78 | 103 | D | 60 | 80
150 | 1800 | NU318C3 | 6318C3 | 445T | 1784 | 58 | 176 | 137 |  |  | 1085 | 441 | 330 | 220 | 260 | 95.7 | 95.2903 | 95.5 | 95.1 | 94.8 | 83.6 | 80.7 | 72.9 | 14 | 8 | 2288 | 46.2 | 84 | 5027.8997 | 3954.5812 | 6 | 5 | 160 | 1570 | 2041 | 640 | 50.05 | 1883 | F | 69 | 83 | D | 60 | 60
150 | 3600 | 6313C3 | 6313C3 | 445TS | 3577 | 47 | 167 | 126 |  |  | 1187.5 | 220 | 165 | 210 | 260 | 95.7 | 95.2903 | 95.7 | 95.3 | 95.2 | 88.1 | 87.4 | 84 | 16 | 9 | 2171 | 37.4 | 85 | 5027.8997 | 3770.9248 | 3 | 2 | 320 | 487 | 633.1 | 133 | 43.16 | 2065 | F | 57 | 71 | D | 40 | 85
200 | 900 | NU324C3 | 6320C3 | N587UZ | 888 | 75 | 241 | 184 |  |  | 1650 | 1182 | 884 | 173 | 218 | 93 | 92.3535 | 94.5 | 93.5 | 94.2 | 83.5 | 80.6 | 73.7 | 29 | 10 | 3133 |  | 72 | 11230.1075 | 6512.6984 |  |  |  | 13800 | 13801 | 4508 | 343 | 4273 | F | 78 | 104 | D | CF | CF
200 | 1200 | NU322 | 6318 | 505UZ | 1188 | 87.5 | 232 | 178 |  |  | 1610 | 884 | 661 | 200 | 210 | 95.8 | 95.3993 | 96.1 | 95.7 | 96 | 84.2 | 82.1 | 75.4 | 14 | 7 | 3016 | 55.8 | 81 | 6541.1273 | 4541.2071 | 6 | 5 | 265 | 5000 | 6500 | 2238 | 146.9 | 3590 | F | 69 | 98 | D | CF | CF
200 | 1200 |  |  | 449TZ | 1185 |  | 239 |  |  |  | 1450 |  |  | 199 | 222 | 95.4 |  |  |  |  | 83 | [18 empty] | 70 |  | D | CF | CF
200 | 1800 | NU318C3 | 6318C3 | 447T | 1784 | 70 | 231 | 178 |  |  | 1450 | 589 | 440 | 240 | 260 | 96.1 | 95.7267 | 96.1 | 95.7 | 95.7 | 84.5 | 81.9 | 74.6 | 13 | 7 | 3003 | 55.8 | 84 | 6054.9428 | 4541.2071 | 5 | 4 | 300 | 2060 | 2678 | 831 | 66.43 | 2328 | F | 78 | 105 | D | 60 | 60
200 | 3600 | 6313C3 | 6313C3 | 447TSS | 3576 | 58 | 222 | 170 |  |  | 1450 | 294 | 220 | 230 | 260 | 96 | 95.6175 | 95.9 | 95.5 | 95.3 | 88 | 86 | 79.8 | 13 | 7 | 2886 | 46.2 | 85 | 6216.6667 | 4784.0459 | 3 | 2 | 600 | 561 | 729.3 | 172 | 53.95 | 2311 | F | 66 | 83 | D | 50 | 75
250 | 900 | NU324C3 | 6320C3 | N587UZ | 887 | 101 | 293 | 226 |  |  | 2100 | 1480 | 1106 | 240 | 285 | 93.6 | 93.0048 | 94 | 92.9 | 93.7 | 85.4 | 82.7 | 74.8 | 29 | 10 | 3809 |  |  | 12752.1368 | 8928.1915 |  |  |  | 14400 | 14400 | 5540 | TBA | 5511 | F | 77 | 105 | D | CF | CF
250 | 1200 | NU324C3 | 6320C3 | 5010UZ | 1188 | 109 | 301 | 236 |  |  | 1825 | 1105 | 827 | 170 | 220 | 95.8 | 95.3993 | 95.8 | 95.4 | 95.7 | 81.2 | 77.5 | 69 | 22 | 12 | 3913 |  |  | 8176.4092 | 6132.3069 | 5 | 4 | 440 | 7950 | 10335 | 2744 | 256 | 4056 | F | 67 | 85 | D | CF | CF
250 | 1800 | NU322 | 6318 | 505UZ | 1788 | 89 | 286 | 222 |  |  | 1800 | 734 | 550 | 230 | 240 | 96.2 | 95.8358 | 95.9 | 95.5 | 95 | 85.1 | 82.3 | 75.3 | 14 | 7 | 3718 |  |  | 7366.9439 | 5980.0574 | 5 | 4 | 500 | 2800 | 3640 | 1017 | 93.2 | 3051 | F | 57 | 78 | D | CF | CF
250 | 3600 | 6313C3 | 6313C3 | 5010USS | 3582 | 53 | 278 | 212 |  |  | 1800 | 366 | 274 | 214 | 247 | 95 | 94.5274 | 95.2 | 94.7 | 95 | 88.6 | 87 | 81.8 | 15 | 8 | 3614 |  |  | 9815.7895 | 7052.521 | 3 | 2 | 1000 | 593 | 770.9 | 210 | 61.7 | 3048 | F | 61 | 70 | D | CF | CF
300 | 1200 | NU324C3 | 6320C3 | 5010UZ | 1188 | 134 | 362 | 285 |  |  | 2200 | 1312.5 | 992 | 160 | 205 | 96.2 | 95.8 | 96 | 95.6 | 95.9 | 80.6 | 76.9 | 68.5 | 16 | 9 | 4706 |  |  | 8840.3326 | 6993.75 |  |  |  | 8800 | 11440 | 3239 |  | 3967 | F | 73 | 104 | D | CF | CF
300 | 1800 | NU324C3 | 6320C3 | 5010UZ | 1788 | 68 | 329 | 248 |  |  | 2000 | 875 | 660 | 150 | 220 | 96.5 | 96.2 | 96.6 | 96.3 | 96.1 | 88.5 | 87.8 | 84.8 | 16 | 9 | 4277 |  |  | 8117.0984 | 5907.764 |  |  |  | 3610 | 4693 | 1197 |  | 3781 | F | 69 | 86 | D | CF | CF
300 | 3600 | 6320C3 | 6320C3 | 5010US | 3582 | 63 | 325 | 245 |  |  | 2200 | 437.5 | 329 | 145 | 255 | 95.8 | 95.4 | 96 | 95.6 | 95.4 | 90.2 | 89.5 | 86 | 16 | 9 | 4225 |  |  | 9811.691 | 6993.75 |  |  |  | 873 | 1134.9 | 1197 |  | 3954 | F | 74 | 93 | D | CF | CF
350 | 1200 |  |  | 5010US | 1185 | 177 | 432 |  |  |  | 2485 |  |  | 167 | 194 | 95.8 | 95 |  |  |  | 79.2 | [18 empty] | 79 | n/a | D | CF | CF
350 | 1800 | 6320C3 | 6320C3 | 5010US | 1788 | 88 | 387 | 294 |  |  | 2500 | 1020.8333 | 769 | 175 | 230 | 96.2 | 95.8 | 96.2 | 95.8 | 95.5 | 88 | 86.9 | 82.3 | 16 | 9 | 5031 |  |  | 10313.7214 | 7735.2911 |  |  |  | 3990 | 5187 | 1197 |  | 3909 | F | 65 | 80 | D | CF | CF
400 | 1800 | 6320C3 | 6320C3 | 5010US | 1788 | 115 | 449 | 345 |  |  | 2800 | 1166.6667 | 879 | 180 | 240 | 96.2 | 95.8 | 96 | 95.6 | 95.3 | 86.7 | 84.9 | 79.5 | 14 | 7 | 5837 |  |  | 11787.1102 | 9325 |  |  |  | 4600 | 5980 | 1546 |  | 3909 | F | 78 | 103 | D | CF | CF
** Safe Stall Times quoted are values which will not in any way cause damage or reduction in life to the rotor, stator or bearings.
*** Subject to change at any time. Please confirm with factory prior to application on constant torque loads
**** Note - 350HP 1200RPM motor is 1.0SF

## 575V EQPIII Data
575V TOSHIBA EQPIII MOTOR DATA | [38 empty] | Data subject to change without notice |  |  |  | 1.3
Note 900RPM data is Standard Efficiency Data | [14 empty] | Guar. |  | Guar. |  |  |  |  | STALL | STALL | Max. |  |  |  |  | -Note #1- |  | TIME | Std | Max. | Max. |  |  |  | Temp. | Temp. | Type | Min. | Max
Rated |  | DE | ODE |  | Full |  |  | 75% |  |  | 3/4 Load |  |  | Eff'y | Eff'y | Eff'y | Eff'y | Eff'y | P.F. | P.F. | P.F. | TIME | TIME | Motor | Max | SOUND | FL | 3/4 Load | (Starts per HR) |  | BTWN | Max. | Toshiba | NEMA | Rotor |  |  | Rise | Rise | of | Speed | Torque
HP: | RPM: | Bearing | Bearing | Frame | Load | Idle | FLC | Current | LRC | FLT | Torque | LRT | BDT | @1.0 | @1.0 | @0.75 | @0.75 | @O.5 | @ 1.0 | @.75 | @0.5 | COLD | HOT | Inrush | KVAR | LEVELS | Watts | Watts | Cold | Hot | STARTS | WK^2 | WK^2 | WK^2 | Inertia | Weight | Ins. | @1.0 | @1.15 | Conn. | @FLT | @ 10Hz
|  |  |  | (#) | RPM | (A) | (A) | (A) | (A) | (lbft) | (lbft) | (%) | (%) | (%) | (%) | (%) | (%) | (%) | (%) | (%) | (%) | (Sec) | (Sec) | (A) |  |  | Loss | Loss | (Sec) | (Sec) | (Sec) | (lbft^2) | (lbft^2) | (lbft^2) | (lbft^2) | (Lbs) | (Cl) | (Deg) | (Deg) | (Y / D) | (Hz) | (%)
[22 empty] | ** | ** | [17 empty] | *** | ***
0.5 | 900 | 6205ZZ | 6205ZZ | 145T | 861 | 1.3 | 1.4 | 1.4 | 6.4 | 3 | 2.3 | 360 | 375 | 67.5 | 63.3803 | 62.4 | 58 | 58.3 | 41 | 33 | 29 | 51 | 21 | 18.2 |  | 48 | 179.5926 | 168.5673 |  |  |  | 198 | 198 |  | TBA | 57 | F | 48 | 50 | Y | CF | CF
0.5 | 1200 | 6305UUC3 | 6305UUC3 | 143T | 1162 | 0.9 | 0.9 | 0.9 | 7.6 | 2.3 | 1.7 | 548 | 560 | 78.8 | 75.5948 | 75 | 71.4 | 72.9 | 52.4 | 43 | 39 | 52 | 30 | 11.7 | 0.8 | 50 | 100.3503 | 93.25 | 35 | 34 |  | 87 | 113.1 |  | 0.1144 | 46 | F | 19 | 20 | Y | 10 | 100
0.5 | 1800 | 6305UUC3 | 6305UUC3 | 143T | 1764 | 0.6 | 0.7 | 0.6 | 8.8 | 1.5 | 1.1 | 670 | 736 | 83 | 80.2708 | 81.5 | 78.6 | 80.1 | 60.6 | 54 | 50 | 44 | 26 | 9.1 | 0.5 | 46 | 76.3976 | 63.5015 | 31 | 30 |  |  |  |  | 0.11245 | 42 | F | 12 | 13 | Y | 10 | 100
0.75 | 900 | 6205ZZ | 6205ZZ | 145T | 860 | 1.3 | 1.6 | 1.5 | 6.4 | 4.6 | 3.4 | 240 | 250 | 70 | 66.0377 | 67.2 | 63.1 | 61.8 | 49 | 40.8 | 30.7 | 51 | 21 | 20.8 |  | 48 | 239.7857 | 204.817 |  |  |  | 198 | 198 |  | TBA | 57 | F | 55 | 65 | Y | CF | CF
0.75 | 1200 | 6305UUC3 | 6305UUC3 | 143T | 1160 | 0.9 | 1.1 | 1 | 7.6 | 3.4 | 2.5 | 365 | 375 | 79.8 | 76.7013 | 78.7 | 75.5 | 74.8 | 61.5 | 52 | 40.7 | 52 | 30 | 14.3 | 0.8 | 50 | 141.6278 | 113.5707 | 35 | 34 |  | 87 | 113.1 |  | 0.1144 | 46 | F | 23 | 29 | Y | 10 | 100
0.75 | 1800 | 6305UUC3 | 6305UUC3 | 143T | 1762 | 0.6 | 0.9 | 0.8 | 8.8 | 2.2 | 1.7 | 448 | 491 | 84.7 | 82.1851 | 82.9 | 80.2 | 81.3 | 72.7 | 60.2 | 52.7 | 44 | 26 | 11.7 | 0.5 | 46 | 101.0667 | 86.5571 | 31 | 30 |  |  |  |  | 0.11245 | 42 | F | 14 | 17 | Y | 10 | 100
0.75 | 3600 | 6305UUC3 | 6305UUC3 | 143T | 3545 | 0.9 | 1.1 | 1 | 16 | 1.1 | 0.8 | 700 | 800 | 80.5 | 77.4783 | 79 | 75.8 | 75.3 | 63.2 | 53.5 | 47.6 | 34 | 20 | 14.3 | 0.8 | 58 | 135.5311 | 111.5459 | 16 | 15 |  |  |  |  | 0.06565 | 53 | F | 19 | 23 | Y | 10 | 100
1 | 900 | 6207ZZ | 6205ZZ | 182T | 862 | 1.4 | 1.7 | 1.4 | 7.8 | 6.1 | 4.5 | 202 | 306 | 74 | 70.3422 | 76.1 | 72.6 | 71.5 | 60 | 51 | 39.9 | 51 | 21 | 22.1 |  | 48 | 262.1081 | 175.7168 |  |  |  | 308 | 308 | 31 | TBA | 82 | F | 40 | 52 | Y | CF | CF
1 | 1200 | 6305UUC3 | 6305UUC3 | 145T | 1152 | 1 | 1.4 | 1.3 | 9.6 | 4.6 | 3.4 | 285 | 320 | 82.4 | 79.5981 | 82 | 79.2 | 78 | 63 | 54.5 | 40.9 | 52 | 28 | 18.2 | 0.6 | 50 | 159.3398 | 122.8171 | 35 | 34 | 33 | 93 | 120.9 | 15 | 0.1365 | 49 | F | 40 | 46 | Y | 10 | 100
1 | 1800 | 6305UUC3 | 6305UUC3 | 143T | 1749 | 0.6 | 1.1 | 0.9 | 8.8 | 3 | 2.2 | 336 | 368 | 85.7 | 83.3171 | 86.1 | 83.8 | 84.1 | 79.1 | 72.7 | 59.8 | 36 | 24 | 14.3 | 0.5 | 46 | 124.4784 | 90.3258 | 31 | 30 | 38 | 37 | 48.1 | 5.8 | 0.11245 | 43 | F | 18 | 21 | Y | 10 | 100
1 | 3600 | 6305UUC3 | 6305UUC3 | 143T | 3526 | 0.9 | 1.2 | 1.1 | 16 | 1.5 | 1.1 | 525 | 600 | 83.3 | 80.6077 | 80.5 | 77.5 | 78.8 | 74.5 | 63.3 | 51.1 | 34 | 20 | 15.6 | 0.8 | 58 | 149.5582 | 135.5311 | 16 | 15 | 75 |  |  |  | 0.06565 | 53 | F | 23 | 29 | Y | 10 | 100
1.5 | 900 | 6207ZZ | 6205ZZ | 184T | 866 | 1.8 | 2.4 | 2.2 | 12 | 9.1 | 6.8 | 206 | 299 | 77 | 73.6138 | 76 | 72.5 | 71.4 | 60.4 | 51.4 | 40.3 | 51 | 21 | 31.2 |  | 46 | 334.2468 | 265.0263 |  |  |  | 340 | 340 | 45 | TBA | 90 | F | 40 | 52 | Y | CF | CF
1.5 | 1200 | 6306UUC3 | 6306UUC3 | 182T | 1168 | 1.2 | 1.9 | 1.6 | 16 | 6.7 | 5 | 266 | 398 | 86.4 | 84.1121 | 86.1 | 83.8 | 84.1 | 68.2 | 60.3 | 46.9 | 50 | 26 | 24.7 | 1.2 | 49 | 176.1389 | 135.4887 | 30 | 29 | 34 | 149 | 193.7 | 23 | 0.2912 | 77 | F | 25 | 41 | Y | 10 | 100
1.5 | 1800 | 6305UUC3 | 6305UUC3 | 145T | 1740 | 0.9 | 1.6 | 1.4 | 16 | 4.5 | 3.4 | 385 | 370 | 86.9 | 84.6813 | 87.1 | 84.9 | 85.7 | 78.7 | 71.1 | 59.2 | 34 | 22 | 20.8 | 0.8 | 46 | 168.687 | 124.2976 | 27 | 26 | 38 | 47 | 61.1 | 8.6 | 0.1495 | 49 | F | 37 | 46 | Y | 10 | 100
1.5 | 3600 | 6305UUC3 | 6305UUC3 | 143T | 3489 | 0.9 | 1.6 | 1.3 | 16 | 2.3 | 1.7 | 350 | 400 | 85.4 | 82.9771 | 84.9 | 82.4 | 82.4 | 81.9 | 75.1 | 63.2 | 34 | 20 | 20.8 | 0.8 | 57 | 191.3044 | 149.2659 | 13 | 12 | 76 | 9.3 | 12.09 | 1.8 | 0.06565 | 53 | F | 28 | 35 | Y | 10 | 100
2 | 900 | 6308UU | 6208UU | 213T | 863 | 1.8 | 2.8 | 2.4 | 12.88 | 12.2 | 9 | 165 | 257 | 80 | 76.9231 | 80.2 | 77.1 | 77.4 | 67.4 | 59.2 | 46.6 | 46 | 19 | 36.4 |  | 48 | 373 | 276.2618 |  |  |  | 455 | 455 | 60 | TBA | 137 | F | 45 | 57 | Y | CF | CF
2 | 1200 | 6306UUC3 | 6306UUC3 | 184T | 1172 | 1.6 | 2.5 | 2.2 | 20 | 9 | 6.7 | 280 | 376 | 88.4 | 86.3956 | 87.7 | 85.6 | 85.3 | 66.7 | 58.1 | 45.6 | 50 | 24 | 32.5 | 1.6 | 50 | 195.7828 | 156.9407 | 27 | 26 | 35 | 167 | 217.1 | 30 | 0.3536 | 86 | F | 23 | 31 | Y | 10 | 100
2 | 1800 | 6305UUC3 | 6305UUC3 | 145T | 1733 | 1.1 | 2.1 | 1.8 | 20 | 6.1 | 4.5 | 380 | 340 | 86.8 | 84.5674 | 87.3 | 85.1 | 86.2 | 80.4 | 73.3 | 61.6 | 34 | 20 | 27.3 | 1.1 | 52 | 226.894 | 162.7869 | 24 | 23 | 39 | 56 | 72.8 | 11 | 0.1729 | 54 | F | 34 | 38 | Y | 10 | 100
2 | 3600 | 6305UUC3 | 6305UUC3 | 145T | 3499 | 1 | 2.1 | 1.7 | 20 | 3 | 2.2 | 350 | 400 | 86.4 | 84.1121 | 86.3 | 84 | 84.4 | 84.1 | 77.7 | 65.8 | 31 | 18 | 27.3 | 1 | 58 | 234.8519 | 177.6396 | 13 | 12 | 77 | 10.6 | 13.78 | 2.4 | 0.07735 | 53 | F | 33 | 39 | Y | 10 | 100
3 | 900 | 6308UU | 6208UU | 215T | 864 | 2.8 | 4.2 | 3.5 | 20.8 | 18.2 | 13.5 | 200 | 265 | 82.5 | 79.7101 | 82 | 79.2 | 79.2 | 65.6 | 58.6 | 46.7 | 41 | 15 | 54.6 |  | 49 | 474.7273 | 368.4512 |  |  |  | 553 | 553 | 87 | TBA | 161 | F | 53 | 65 | Y | CF | CF
3 | 1200 | 6308C3 | 6308C3 | 213T | 1167 | 1.7 | 3.2 | 2.6 | 25.6 | 13.5 | 10.1 | 279 | 352 | 90.3 | 88.5815 | 91 | 89.4 | 89.9 | 78 | 70 | 57.7 | 48 | 20 | 41.6 | 1.6 | 50 | 240.4053 | 166.0055 | 24 | 23 | 36 | 260 | 338 | 44 | 0.65 | 125 | F | 22 | 27 | Y | 10 | 100
3 | 1800 | 6306UUC3 | 6306UUC3 | 182T | 1754 | 1.2 | 3 | 2.4 | 25.6 | 9 | 6.7 | 259 | 373 | 89.5 | 87.6592 | 89.7 | 87.9 | 88.6 | 84.2 | 79 | 68.2 | 28 | 15 | 39 | 1.2 | 54 | 262.5587 | 192.7375 | 21 | 20 | 40 | 81 | 105.3 | 17 | 0.3185 | 77 | F | 34 | 41 | Y | 10 | 100
3 | 3600 | 6306UUC3 | 6306UUC3 | 182T | 3509 | 0.9 | 2.8 | 2.2 | 25.6 | 4.5 | 3.3 | 248 | 388 | 88.8 | 86.8545 | 88.9 | 87 | 87.6 | 91.1 | 87.9 | 81 | 24 | 12 | 36.4 | 0.8 | 59 | 282.2703 | 209.5765 | 11 | 10 | 80 | 18.6 | 24.18 | 3.5 | 0.11115 | 77 | F | 25 | 30 | Y | 10 | 100
5 | 900 | 6309UU | 6208UU | 254T | 874 | 3.1 | 6.1 | 4.9 | 27.2 | 30 | 22.4 | 156 | 214 | 86.5 | 84.2259 | 87.3 | 85.1 | 86 | 70.9 | 65.2 | 54.8 | 31 | 11 | 79.3 |  | 49 | 582.1387 | 406.9674 |  |  |  | 985 | 985 | 142 | TBA | 240 | F | 47 | 59 | Y | CF | CF
5 | 1200 | 6308C3 | 6308C3 | 215T | 1165 | 2.5 | 5.2 | 4.3 | 36.8 | 22.5 | 16.8 | 279 | 376 | 90.1 | 88.3507 | 89.7 | 87.9 | 87.4 | 79.4 | 72.7 | 60.6 | 48 | 18 | 67.6 | 4.9 | 49 | 409.8446 | 321.2291 | 20 | 19 | 37 | 305 | 396.5 | 71 | 0.9555 | 153 | F | 32 | 41 | Y | 10 | 100
5 | 1800 | 6306UUC3 | 6306UUC3 | 184T | 1737 | 1.7 | 4.9 | 3.7 | 36.8 | 15.1 | 11.2 | 265 | 290 | 88.4 | 86.3956 | 89.7 | 87.9 | 89.4 | 86.7 | 83.6 | 75.5 | 28 | 13 | 63.7 | 1.7 | 55 | 489.457 | 321.2291 | 17 | 16 | 42 | 99 | 128.7 | 27 | 0.4329 | 101 | F | 56 | 79 | Y | 30 | 90
5 | 3600 | 6306UUC3 | 6306UUC3 | 184T | 3502 | 1.2 | 4.5 | 3.5 | 36.8 | 7.5 | 5.6 | 265 | 357 | 89 | 87.0841 | 89.1 | 87.2 | 87.7 | 92.5 | 90.4 | 84.8 | 24 | 12 | 58.5 | 1.2 | 60 | 461.0112 | 342.2306 | 9 | 8 | 83 | 25.2 | 32.76 | 5.7 | 0.1924 | 99 | F | 45 | 56 | Y | 10 | 100
7.5 | 900 | 6309UU | 6208UU | 256T | 878 | 5.1 | 9.4 | 7.7 | 47.2 | 44.8 | 33.4 | 170 | 244 | 87.5 | 85.3659 | 88 | 85.9 | 87.3 | 68.4 | 61.9 | 50.7 | 37 | 12 | 122.2 |  | 50 | 799.2857 | 572.2159 |  |  |  | 1050 | 1050 | 208 | TBA | 299 | F | 37 | 46 | D | CF | CF
7.5 | 1200 | 6309C3 | 6308C3 | 254T | 1179 | 3.6 | 7.8 | 6.3 | 50.8 | 33.4 | 24.9 | 218 | 340 | 92 | 90.5512 | 91.8 | 91.1 | 90.6 | 78.6 | 73.2 | 62.7 | 48 | 20 | 101.4 | 3.5 | 51 | 486.5217 | 374.8284 | 17 | 16 | 39 | 640 | 832 | 104 | 2.314 | 222 | F | 31 | 38 | D | 10 | 100
7.5 | 1800 | 6308C3 | 6308C3 | 213T | 1752 | 2.9 | 7.4 | 5.8 | 50.8 | 22.5 | 16.7 | 280 | 290 | 90.9 | 89.2752 | 91.2 | 90.4 | 90.3 | 84 | 79 | 69 | 24 | 12 | 96.2 | 2.8 | 57 | 560.1155 | 404.9013 | 15 | 14 | 44 | 155 | 201.5 | 39 | 1.0205 | 153 | F | 43 | 60 | D | 20 | 90
7.5 | 3600 | 6308C3 | 6308ZC3 | 213T | 3515 | 2 | 7 | 5.4 | 50.8 | 11.2 | 8.4 | 213 | 310 | 90.5 | 88.8126 | 90.3 | 89.4 | 89 | 88.5 | 85.8 | 79 | 24 | 12 | 91 | 2 | 62 | 587.3204 | 450.76 | 8 | 7 | 88 | 29.6 | 38.48 | 8.3 | 0.5109 | 165 | F | 48 | 60 | D | 10 | 100
10 | 900 | 6310C3 | 6310CZZ3 | 284T | 879 | 6.6 | 12.2 | 10.1 | 64 | 59.7 | 44.5 | 205 | 244 | 88.5 | 86.5103 | 89.1 | 87.2 | 87.5 | 69.2 | 62.5 | 51.1 | 35 | 11 | 158.6 |  | 50 | 969.3785 | 684.4613 |  |  |  | 1700 | 1700 | 273 | TBA | 416 | F | 32 | 39 | D | CF | CF
10 | 1200 | 6309C3 | 6308C3 | 256T | 1176 | 4.2 | 10.2 | 8.1 | 64.8 | 44.6 | 33.3 | 234 | 283 | 92.5 | 91.133 | 92.8 | 92.1 | 92 | 79.2 | 74.7 | 64.8 | 48 | 18 | 132.6 | 4.1 | 52 | 604.8649 | 434.0948 | 16 | 15 | 41 | 675 | 877.5 | 137 | 2.613 | 251 | F | 38 | 49 | D | 10 | 100
10 | 1800 | 6308C3 | 6308C3 | 215T | 1746 | 3.2 | 9.5 | 7.5 | 64.8 | 30.1 | 22.4 | 290 | 295 | 90.9 | 89.2752 | 91.3 | 90.5 | 90.4 | 86.5 | 82 | 73 | 22 | 10 | 123.5 | 3.2 | 55 | 746.8207 | 533.149 | 14 | 13 | 46 | 163 | 211.9 | 51 | 1.1375 | 168 | F | 47 | 64 | D | 20 | 90
10 | 3600 | 6308C3 | 6308C3 | 215T | 3510 | 2.3 | 9.2 | 7.1 | 64.8 | 15 | 11.1 | 212 | 300 | 90.3 | 88.5815 | 90 | 89.1 | 88 | 89.7 | 87.6 | 81.7 | 22 | 10 | 119.6 | 2.3 | 62 | 801.3511 | 621.6667 | 7 | 6 | 92 | 37.5 | 48.75 | 11 | 0.7046 | 196 | F | 59 | 74 | D | 60 | 80
15 | 900 | 6310C3 | 6310CZZ3 | 286T | 877 | 9.6 | 17.9 | 14.8 | 79.2 | 89.8 | 66.9 | 214 | 226 | 89.5 | 88.57 | 89.3 | 87.4 | 87.9 | 70 | 63.6 | 52.6 | 39 | 14 | 232.7 |  | 55 | 1312.7933 | 1005.5963 |  |  |  | 1880 | 1880 | 400 | TBA | 404 | F | 47 | 61 | D | CF | CF
15 | 1200 | 6310C3 | 6310C3 | 284T | 1173 | 5.7 | 14.8 | 11.7 | 92.8 | 67.1 | 50.1 | 208 | 277 | 92.3 | 91.5947 | 92.5 | 91.8 | 92 | 82 | 77.7 | 68.3 | 45 | 18 | 192.4 | 5.6 | 59 | 933.5103 | 680.473 | 13 | 12 | 44 | 1120 | 1456 | 200 | 5.2 | 374 | F | 45 | 58 | D | 30 | 85
15 | 1800 | 6309C3 | 6308C3 | 254T | 1774 | 5.3 | 14.5 | 11.4 | 88 | 44.4 | 33.2 | 229 | 254 | 92.4 | 91.7031 | 92.6 | 91.9 | 91.8 | 83.6 | 79.7 | 71 | 24 | 12 | 188.5 | 5.2 | 61 | 920.3896 | 670.6749 | 12 | 11 | 50 | 296 | 384.8 | 75 | 2.106 | 234 | F | 45 | 56 | D | 10 | 100
15 | 3600 | 6309C3 | 6308C3 | 254T | 3533 | 2.7 | 13.3 | 10 | 92.8 | 22.3 | 16.6 | 220 | 290 | 91.6 | 91 | 92 | 91.3 | 91.6 | 91.9 | 91.8 | 91.1 | 24 | 11 | 172.9 | 2.7 | 65 | 1026.1572 | 729.7826 | 7 | 6 | 100 | 40 | 52 | 16 | 1.378 | 266 | F | 56 | 75 | D | 30 | 90
20 | 900 | 6312C3 | 6312ZZC3 | 324T | 879 | 11 | 23.6 | 19 | 114 | 119 | 89.1 | 225 | 204 | 89.5 | 88.57 | 89.9 | 88.1 | 88.9 | 70.8 | 65.7 | 55.4 | 28 | 12 | 306.8 |  | 55 | 1750.3911 | 1257.1635 |  |  |  | 2580 | 2580 | 525 | TBA | 591 | F | 48 | 62 | D | CF | CF
20 | 1200 | 6310C3 | 6310C3 | 286T | 1170 | 8 | 19.4 | 15.1 | 116 | 89.7 | 66.9 | 205 | 275 | 92.3 | 91.5947 | 92.6 | 91.9 | 92.2 | 83.5 | 80.2 | 72.2 | 44 | 16 | 252.2 | 7.9 | 59 | 1244.6804 | 894.2333 | 12 | 11 | 48 | 1250 | 1625 | 262 | 6.37 | 404 | F | 50 | 66 | D | 30 | 85
20 | 1800 | 6309C3 | 6308C3 | 256T | 1772 | 6.5 | 19 | 14.8 | 116 | 59.3 | 44.3 | 225 | 240 | 93.1 | 92.462 | 93.4 | 92.8 | 93 | 84.9 | 81.4 | 73.3 | 21 | 9 | 247 | 6.4 | 61 | 1105.7787 | 790.7281 | 11 | 10 | 55 | 344 | 447.2 | 99 | 2.873 | 285 | F | 51 | 66 | D | 20 | 90
20 | 3600 | 6309C3 | 6308C3 | 256T | 3535 | 3.3 | 17.4 | 13.1 | 116 | 29.7 | 22.2 | 250 | 280 | 92.5 | 91.8114 | 93.2 | 92.6 | 93.2 | 92.9 | 92.3 | 88.9 | 21 | 9 | 226.2 | 3.3 | 72 | 1209.7297 | 816.4378 | 6 | 5 | 110 | 50.6 | 65.78 | 21 | 2.08 | 312 | F | 56 | 80 | D | 60 | 80
25 | 900 | 6312C3 | 6312ZZC3 | 326T | 881 | 14.6 | 28.7 | 23.4 | 146 | 149 | 111 | 250 | 236 | 91 | 90.1883 | 90.9 | 89.3 | 88.7 | 71.6 | 66 | 55.3 | 30 | 10 | 373.1 |  | 59 | 1844.5055 | 1400.2888 |  |  |  | 2770 | 2770 | 647 | TBA | 683 | F | 59 | 73 | D | CF | CF
25 | 1200 | 6312C3 | 6312C3 | 324T | 1175 | 10 | 24.9 | 19.6 | 146 | 112 | 83.3 | 245 | 255 | 92.9 | 92.2451 | 93.5 | 92.9 | 93 | 80.9 | 76.8 | 67.7 | 42 | 20 | 323.7 | 9.9 | 59 | 1425.3498 | 972.393 | 11 | 10 | 51 | 1730 | 2249 | 324 | 8.45 | 496 | F | 46 | 61 | D | 10 | 100
25 | 1800 | 6310C3 | 6310C3 | 284T | 1770 | 8.4 | 23.4 | 18.1 | 146 | 74.2 | 55.4 | 240 | 260 | 93.5 | 92.8962 | 93.7 | 93.1 | 93.1 | 85.5 | 82.6 | 75 | 21 | 8 | 304.2 | 8.3 | 67 | 1296.5241 | 940.4616 | 10 | 9 | 58 | 400 | 520 | 122 | 3.12 | 370 | F | 51 | 67 | D | 30 | 90
25 | 3600 | 6310C3 | 6310C3 | 284TS | 3529 | 4 | 21.7 | 16.3 | 146 | 37.2 | 27.8 | 260 | 250 | 92.4 | 91.7031 | 93 | 92.4 | 92 | 93.2 | 92.4 | 89.6 | 21 | 8 | 282.1 | 4 | 81 | 1533.9827 | 1052.8226 | 6 | 5 | 115 | 106 | 137.8 | 26 | 3.25 | 411 | F | 53 | 75 | D | 60 | 80
30 | 900 | 6314C3 | 6312C3 | 364T | 879 | 16.3 | 33.3 | 26.8 | 174 | 179 | 134 | 252 | 203 | 91 | 90.1883 | 91 | 89.4 | 89.5 | 74.2 | 69 | 58.4 | 29 | 10 | 432.9 |  | 59 | 2213.4066 | 1660.0549 |  |  |  | 2900 | 2900 | 769 | TBA | 816 | F | 53 | 67 | D | CF | CF
30 | 1200 | 6312C3 | 6312C3 | 326T | 1177 | 11.2 | 29.6 | 23.2 | 174 | 134 | 100 | 245 | 254 | 93.6 | 93.0048 | 94 | 93.4 | 93.7 | 81.2 | 77.2 | 68.1 | 42 | 18 | 384.8 | 11.1 | 61 | 1530.2564 | 1071.383 | 10 | 9 | 53 | 1840 | 2392 | 384 | 10.01 | 539 | F | 49 | 63 | D | 20 | 90
30 | 1800 | 6310C3 | 6310C3 | 286T | 1770 | 10.4 | 28.1 | 21.8 | 174 | 89 | 66.5 | 255 | 275 | 93.4 | 93 | 93.6 | 93 | 93 | 85.7 | 82.7 | 75.6 | 20 | 7 | 365.3 | 10.3 | 69 | 1581.4561 | 1147.6923 | 9 | 8 | 60 | 443 | 575.9 | 144 | 4.03 | 404 | F | 63 | 81 | D | 60 | 80
30 | 3600 | 6310C3 | 6310C3 | 286TS | 3524 | 4.8 | 26 | 19.5 | 174 | 44.7 | 33.3 | 260 | 250 | 92.4 | 91.7031 | 93.1 | 92.5 | 92.1 | 93.5 | 92.8 | 90.5 | 20 | 7 | 338 | 4.7 | 82 | 1840.7792 | 1244.0011 | 5 | 4 | 120 | 112 | 145.6 | 31 | 3.51 | 462 | F | 58 | 75 | D | 60 | 80
40 | 900 | 6314C3 | 6312C3 | 365T | 877 | 19.6 | 43.2 | 34.3 | 218 | 239 | 178 | 220 | 213 | 91 | 90.1883 | 91.7 | 90.2 | 91.3 | 76.2 | 71.5 | 61.6 | 29 | 11 | 561.6 |  | 60 | 2951.2088 | 2025.6707 |  |  |  | 3170 | 3170 | 1007 | TBA | 920 | F | 50 | 64 | D | CF | CF
40 | 1200 | 6314C3 | 6312C3 | 364T | 1176 | 11.6 | 37.5 | 28.9 | 232 | 179 | 133 | 245 | 260 | 94 | 93.6 | 94.6 | 94.1 | 94.5 | 84.9 | 82.2 | 74.8 | 40 | 20 | 487.5 | 11.6 | 66 | 1904.6809 | 1277.5053 | 10 | 9 | 57 | 1900 | 2470 | 503 | 17.68 | 714 | F | 51 | 69 | D | 30 | 85
40 | 1800 | 6312C3 | 6312C3 | 324T | 1770 | 12.8 | 38.3 | 29.6 | 232 | 119 | 88.6 | 250 | 260 | 94 | 93.6 | 94.4 | 93.9 | 94.1 | 83.2 | 80.4 | 72.9 | 25 | 11 | 497.9 | 12.7 | 71 | 1904.6809 | 1327.6271 | 9 | 8 | 65 | 593 | 770.9 | 189 | 8.45 | 568 | F | 54 | 67 | D | 30 | 80
40 | 3600 | 6312C3 | 6312C3 | 324TS | 3535 | 8.8 | 35.9 | 27 | 232 | 59.4 | 44.4 | 260 | 240 | 93.1 | 92.462 | 93.4 | 92.8 | 92.8 | 89.7 | 89.2 | 84.3 | 28 | 11 | 466.7 | 8.7 | 80 | 2211.5575 | 1581.4561 | 5 | 4 | 130 | 137 | 178.1 | 40 | 5.33 | 574 | F | 63 | 87 | D | 40 | 85
50 | 900 | 6317C3 | 6313C3 | 404T | 879 | 16 | 49.6 | 37.6 | 282 | 299 | 223 | 150 | 225 | 91 | 90.1883 | 92 | 90.6 | 91.3 | 83 | 81.2 | 74.6 | 29 | 11 | 644.8 |  | 66 | 3689.011 | 2432.6087 |  |  |  | 4300 | 4300 | 1241 | TBA | 1150 | F | 55 | 74 | D | CF | CF
50 | 1200 | 6314C3 | 6312C3 | 365T | 1175 | 14.8 | 47.9 | 37.2 | 290 | 223 | 167 | 250 | 264 | 93.6 | 93.6 | 94.4 | 93.9 | 94.3 | 83.5 | 79.9 | 71 | 40 | 18 | 622.7 | 14.7 | 67 | 2550.4274 | 1659.5339 | 9 | 8 | 64 | 2090 | 2717 | 620 | 22.36 | 793 | F | 63 | 83 | D | 30 | 80
50 | 1800 | 6312C3 | 6312C3 | 326T | 1771 | 16 | 47.3 | 36.6 | 290 | 148 | 111 | 260 | 240 | 94 | 93.6 | 94.2 | 93.7 | 93.9 | 84.2 | 81.4 | 74.5 | 22 | 10 | 614.9 | 16 | 71 | 2380.8511 | 1722.4522 | 8 | 7 | 72 | 625 | 812.5 | 232 | 9.23 | 595 | F | 51 | 67 | D | 30 | 80
50 | 3600 | 6312C3 | 6312C3 | 326TS | 3533 | 9.6 | 44.3 | 33.6 | 290 | 74.3 | 55.5 | 270 | 270 | 93 | 92.3535 | 93.3 | 92.7 | 92.6 | 90.9 | 89.7 | 86 | 23 | 10 | 575.9 | 9.5 | 81 | 2807.5269 | 2008.9228 | 5 | 4 | 145 | 156 | 202.8 | 49 | 6.37 | 690 | F | 67 | 90 | D | 60 | 75
60 | 900 | 6317C3 | 6313C3 | 405T | 880 | 21.6 | 60.8 | 47.5 | 344 | 358 | 267 | 190 | 230 | 91 | 90.1883 | 91.3 | 89.7 | 91.3 | 81.2 | 77.8 | 69.9 | 29 | 10 | 790.4 |  | 68 | 4426.8132 | 3198.8938 |  |  |  | 4600 | 4600 | 1473 | TBA | 1495 | F | 65 | 90 | D | CF | CF
60 | 1200 | 6317C3 | 6313C3 | 404T | 1187 | 20.8 | 58.1 | 45.7 | 348 | 265 | 198 | 210 | 244 | 95 | 94.5274 | 95.1 | 94.6 | 94.6 | 81.4 | 77.5 | 69.5 | 38 | 20 | 755.3 | 20.7 | 70 | 2355.7895 | 1729.6845 | 8 | 7 | 75 | 2630 | 3419 | 735 | 31.59 | 1144 | F | 58 | 70 | D | 30 | 90
60 | 1800 | 6314C3 | 6312C3 | 364T | 1777 | 17.6 | 56.3 | 43.4 | 348 | 177 | 133 | 216 | 274 | 95.1 | 94.6363 | 95.2 | 94.7 | 94.6 | 84 | 81.5 | 74.9 | 21 | 8 | 731.9 | 17.5 | 72 | 2306.2461 | 1692.605 | 7 | 6 | 85 | 770 | 1001 | 275 | 13.91 | 741 | F | 51 | 62 | D | 60 | 50
60 | 3600 | 6312C3 | 6312C3 | 364TS | 3547 | 14.8 | 53.8 | 41 | 348 | 88.8 | 66.4 | 230 | 280 | 93.8 | 93.222 | 94 | 93.4 | 93.7 | 89 | 87.5 | 82.6 | 29 | 10 | 699.4 | 14.7 | 85 | 2958.5501 | 2142.766 | 4 | 3 | 170 | 169 | 219.7 | 58 | 10.01 | 845 | F | 63 | 85 | D | 40 | 80
75 | 900 | NU318C3 | 6318C3 | 444T | 882 | 26.4 | 76.4 | 59.2 | 432 | 446 | 333 | 175 | 250 | 91.7 | 90.9452 | 92.3 | 90.9 | 92 | 80.2 | 77.1 | 68.2 | 29 | 10 | 993.2 |  | 69 | 5064.1767 | 3500.6636 |  |  |  | 6170 | 6170 | 1814 | TBA | 1932 | F | 71 | 98 | D | CF | CF
75 | 1200 | 6317C3 | 6313C3 | 405T | 1186 | 25.6 | 72.5 | 56.5 | 434 | 332 | 248 | 210 | 241 | 94.9 | 94.4185 | 95.1 | 94.6 | 94.5 | 81.6 | 78.4 | 69.6 | 28 | 15 | 942.5 | 25.5 | 70 | 3006.7966 | 2162.1057 | 8 | 7 | 79 | 2930 | 3809 | 904 | 62.53 | 1292 | F | 46 | 60 | D | 30 | 90
75 | 1800 | 6314C3 | 6312C3 | 365T | 1775 | 23.2 | 70.3 | 54.6 | 434 | 222 | 166 | 200 | 270 | 95.3 | 94.8542 | 95.5 | 95.1 | 95 | 83.8 | 80.8 | 73.9 | 20 | 7 | 913.9 | 23.1 | 79 | 2759.3389 | 1977.2906 | 7 | 6 | 90 | 862 | 1120.6 | 338 | 17.68 | 853 | F | 58 | 74 | D | 60 | 30
75 | 3600 | 6312C3 | 6312C3 | 365TS | 3540 | 17.6 | 67.9 | 51.6 | 434 | 111 | 83.1 | 260 | 270 | 93.5 | 92.8962 | 93.8 | 93.2 | 93.4 | 88.5 | 87 | 82 | 21 | 8 | 882.7 | 17.5 | 85 | 3889.5722 | 2773.6407 | 4 | 3 | 180 | 194 | 252.2 | 71 | 11.57 | 908 | F | 60 | 80 | D | 60 | 80
100 | 900 | NU318C3 | 6318C3 | 445T | 881 | 30.4 | 97.4 | 76 | 576 | 596 | 445 | 190 | 240 | 92.4 | 91.7031 | 93 | 91.7 | 92.8 | 83.2 | 79.5 | 73.1 | 27 | 9 | 1266.2 |  | 69 | 6135.9307 | 4211.2903 |  |  |  | 7080 | 7080 | 2372 | 85.4 | 2291 | F | 71 | 98 | D | CF | CF
100 | 1200 | NU318C3 | 6318C3 | 444T | 1183 | 32.8 | 97.9 | 75.5 | 580 | 444 | 332 | 200 | 225 | 95.5 | 95.0722 | 95.7 | 95.3 | 95.2 | 80.1 | 77.8 | 69.8 | 18 | 9 | 1272.7 | 32.6 | 76 | 3515.1832 | 2513.9498 | 7 | 6 | 97 | 3300 | 4290 | 1181 | 57.85 | 1764 | F | 62 | 81 | D | 60 | 85
100 | 1800 | 6317C3 | 6313C3 | 405T | 1776 | 29.6 | 93.4 | 72.4 | 580 | 296 | 221 | 200 | 256 | 95.4 | 94.9632 | 95.6 | 95.2 | 95.3 | 84.1 | 81.2 | 74.3 | 19 | 9 | 1214.2 | 29.5 | 79 | 3597.065 | 2575.1046 | 6 | 5 | 110 | 1062 | 1380.6 | 441 | 28.47 | 1324 | F | 69 | 87 | D | 60 | 80
100 | 3600 | 6313C3 | 6313C3 | 405TS | 3557 | 21.2 | 89.8 | 68.6 | 580 | 148 | 110 | 215 | 260 | 95 | 94.5274 | 95 | 94.5 | 94.8 | 87.8 | 86.2 | 81 | 20 | 10 | 1167.4 | 21.1 | 85 | 3926.3158 | 2944.7368 | 4 | 3 | 220 | 262 | 340.6 | 92 | 20.02 | 1357 | F | 67 | 89 | D | 60 | 75
125 | 900 | NU322C3 | 6318C3 | 505UZ | 885 | 42 | 125 | 96.9 | 652 | 742 | 554 | 125 | 220 | 93.6 | 93.0048 | 93.8 | 92.7 | 93.3 | 80.2 | 77.3 | 69.7 | 30 | 12 | 1625 |  | 69 | 6376.0684 | 4622.7345 |  |  |  | 7900 | 7900 | 2919 | 80.7 | 2943 | F | 64 | 83 | D | CF | CF
125 | 1200 | NU318C3 | 6318C3 | 445T | 1186 | 51.2 | 124 | 95.4 | 726 | 553 | 414 | 206 | 230 | 95.5 | 95.0722 | 95.6 | 95.2 | 95.5 | 79.1 | 77 | 69 | 15 | 8 | 1612 | 51 | 74 | 4393.9791 | 3218.8808 | 7 | 6 | 120 | 3560 | 4628 | 1452 | 66.43 | 1919 | F | 67 | 88 | D | 60 | 85
125 | 1800 | NU318C3 | 6318C3 | 444T | 1785 | 36.8 | 116 | 90.5 | 726 | 368 | 275 | 216 | 256 | 95.7 | 95.2903 | 95.7 | 95.3 | 95 | 84.1 | 81.1 | 73.3 | 18 | 11 | 1508 | 36.6 | 84 | 4189.9164 | 3142.4373 | 6 | 5 | 140 | 1490 | 1937 | 542 | 44.72 | 1762 | F | 61 | 79 | D | 60 | 70
125 | 3600 | 6313C3 | 6313C3 | 444TS | 3575 | 29.2 | 111 | 84.3 | 726 | 184 | 137 | 215 | 265 | 95.3 | 94.8542 | 95.2 | 94.7 | 94.8 | 88.2 | 87.5 | 84.3 | 19 | 10 | 1443 | 29 | 85 | 4598.8982 | 3526.2605 | 4 | 3 | 275 | 430 | 559 | 113 | 36.27 | 1873 | F | 62 | 75 | D | 30 | 85
150 | 900 | NU322C3 | 6318C3 | 505UZ | 884 | 53 | 150 | 115.2 | 828 | 891 | 665 | 130 | 225 | 93.6 | 93.0048 | 93.7 | 92.5 | 93.5 | 80.2 | 78.1 | 69.5 | 33 | 14 | 1950 |  | 71 | 7651.2821 | 5642.7695 |  |  |  | 10200 | 10200 | 3456 | 92 | 4213 | F | 68 | 88 | D | CF | CF
150 | 1200 | NU318C3 | 6318C3 | 447T | 1184 | 52 | 145 | 112.7 | 868 | 665 | 497 | 220 | 245 | 95.8 | 95.3993 | 96.2 | 95.8 | 96.1 | 81.1 | 77.7 | 68.7 | 13 | 7 | 1885 | 51.7 | 77 | 4905.8455 | 3315.1247 | 6 | 5 | 140 | 3800 | 4940 | 1719 | 76.31 | 2132 | F | 78 | 103 | D | 60 | 80
150 | 1800 | NU318C3 | 6318C3 | 445T | 1784 | 46.4 | 140 | 109.3 | 868 | 441 | 330 | 220 | 260 | 95.7 | 95.2903 | 95.5 | 95.1 | 94.8 | 83.6 | 80.7 | 72.9 | 14 | 8 | 1820 | 46.2 | 84 | 5027.8997 | 3954.5812 | 6 | 5 | 160 | 1570 | 2041 | 640 | 50.05 | 1883 | F | 69 | 83 | D | 60 | 60
150 | 3600 | 6313C3 | 6313C3 | 445TS | 3577 | 37.6 | 133 | 100.8 | 950 | 220 | 165 | 210 | 260 | 95.7 | 95.2903 | 95.7 | 95.3 | 95.2 | 88.1 | 87.4 | 84 | 16 | 9 | 1729 | 37.4 | 85 | 5027.8997 | 3770.9248 | 3 | 2 | 320 | 487 | 633.1 | 133 | 43.16 | 2065 | F | 57 | 71 | D | 40 | 85
200 | 900 | NU324C3 | 6320C3 | N587UZ | 888 | 60 | 193 | 147.5 | 1320 | 1182 | 884 | 173 | 218 | 93 | 92.3535 | 94.5 | 93.5 | 94.2 | 83.5 | 80.6 | 73.7 | 29 | 10 | 2509 |  | 72 | 11230.1075 | 6512.6984 |  |  |  | 13800 | 13801 | 4508 | 343 | 4273 | F | 78 | 104 | D | CF | CF
200 | 1200 | NU322 | 6318 | 505UZ | 1188 | 70 | 186 | 142.4 | 1288 | 884 | 661 | 200 | 210 | 95.8 | 95.3993 | 96.1 | 95.7 | 96 | 84.2 | 82.1 | 75.4 | 14 | 7 | 2418 | 55.8 | 81 | 6541.1273 | 4541.2071 | 6 | 5 | 265 | 5000 | 6500 | 2238 | 146.9 | 3590 | F | 69 | 98 | D | CF | CF
200 | 1200 |  |  | 449TZ | 1185 |  | 191 |  | 1160 |  |  | 199 | 222 | 95.4 |  |  |  |  | 83 | [18 empty] | 70 |  | D | CF | CF
200 | 1800 | NU318C3 | 6318C3 | 447T | 1784 | 56 | 184 | 142.8 | 1160 | 589 | 440 | 240 | 260 | 96.1 | 95.7267 | 96.1 | 95.7 | 95.7 | 84.5 | 81.9 | 74.6 | 13 | 7 | 2392 | 55.8 | 84 | 6054.9428 | 4541.2071 | 5 | 4 | 300 | 2060 | 2678 | 831 | 66.43 | 2328 | F | 78 | 105 | D | 60 | 60
200 | 3600 | 6313C3 | 6313C3 | 447TSS | 3576 | 46.4 | 177 | 136.2 | 1160 | 294 | 220 | 230 | 260 | 96 | 95.6175 | 95.9 | 95.5 | 95.3 | 88 | 86 | 79.8 | 13 | 7 | 2301 | 46.2 | 85 | 6216.6667 | 4784.0459 | 3 | 2 | 600 | 561 | 729.3 | 172 | 53.95 | 2311 | F | 66 | 83 | D | 50 | 75
250 | 900 | NU324C3 | 6320C3 | N587UZ | 887 | 81 | 234 | 180.7 | 1680 | 1480 | 1106 | 240 | 285 | 93.6 | 93.0048 | 94 | 92.9 | 93.7 | 85.4 | 82.7 | 74.8 | 29 | 10 | 3042 |  |  | 12752.1368 | 8928.1915 |  |  |  | 14400 | 14400 | 5540 | TBA | 5511 | F | 77 | 105 | D | CF | CF
250 | 1200 | NU324C3 | 6320C3 | 5010UZ | 1188 | 87 | 241 | 189.2 | 1460 | 1105 | 827 | 170 | 220 | 95.8 | 95.3993 | 95.8 | 95.4 | 95.7 | 81.2 | 77.5 | 69 | 22 | 12 | 3133 |  |  | 8176.4092 | 6132.3069 | 5 | 4 | 440 | 7950 | 10335 | 2744 | 256 | 4056 | F | 67 | 85 | D | CF | CF
250 | 1800 | NU322 | 6318 | 505UZ | 1788 | 71 | 229 | 178 | 1440 | 734 | 550 | 230 | 240 | 96.2 | 95.8358 | 95.9 | 95.5 | 95 | 85.1 | 82.3 | 75.3 | 14 | 7 | 2977 |  |  | 7366.9439 | 5980.0574 | 5 | 4 | 500 | 2800 | 3640 | 1017 | 93.2 | 3051 | F | 57 | 78 | D | CF | CF
250 | 3600 | 6313C3 | 6313C3 | 5010USS | 3582 | 42 | 222 | 169.6 | 1440 | 366 | 274 | 214 | 247 | 95 | 94.5274 | 95.2 | 94.7 | 95 | 88.6 | 87 | 81.8 | 15 | 8 | 2886 |  |  | 9815.7895 | 7052.521 | 3 | 2 | 1000 | 593 | 770.9 | 210 | 61.7 | 3048 | F | 61 | 70 | D | CF | CF
300 | 1200 | NU324C3 | 6320C3 | 5010UZ | 1188 | 107 | 290 | 228.3 | 1760 | 1312.5 | 992 | 160 | 205 | 96.2 | 95.8 | 96 | 95.6 | 95.9 | 80.6 | 76.9 | 68.5 | 16 | 9 |  |  |  | 8840.3326 | 6993.75 |  |  |  | 8800 | 11440 | 3239 |  | 3967 | F | 73 | 104 | D | CF | CF
300 | 1800 | NU324C3 | 6320C3 | 5010UZ | 1788 | 54 | 263 | 198.7 | 1600 | 875 | 660 | 150 | 220 | 96.5 | 96.2 | 96.6 | 96.3 | 96.1 | 88.5 | 87.8 | 84.8 | 16 | 9 |  |  |  | 8117.0984 | 5907.764 |  |  |  | 3610 | 4693 | 1197 |  | 3781 | F | 69 | 86 | D | CF | CF
300 | 3600 | 6320C3 | 6320C3 | 5010US | 3582 | 50 | 260 | 196.2 | 1760 | 437.5 | 329 | 145 | 255 | 95.8 | 95.4 | 96 | 95.6 | 95.4 | 90.2 | 89.5 | 86 | 16 | 9 |  |  |  | 9811.691 | 6993.75 |  |  |  | 873 | 1134.9 | 1197 |  | 3954 | F | 74 | 93 | D | CF | CF
350 | 1200 |  |  | 5010US | 1185 | 142 | 346 |  | 1988 |  |  | 167 | 194 | 95.8 |  |  |  |  | 79.2 | [18 empty] | 79 | n/a | D | CF | CF
350 | 1800 | 6320C3 | 6320C3 | 5010US | 1788 | 70 | 310 | 235.2 | 2000 | 1020.8333 | 769 | 175 | 230 | 96.2 | 95.8 | 96.2 | 95.8 | 95.5 | 88 | 86.9 | 82.3 | 16 | 9 |  |  |  | 10313.7214 | 7735.2911 |  |  |  | 3990 | 5187 | 1197 |  | 3909 | F | 65 | 80 | D | CF | CF
400 | 1800 | 6320C3 | 6320C3 | 5010US | 1788 | 92 | 359 | 275.7 | 2240 | 1166.6667 | 879 | 180 | 240 | 96.2 | 95.8 | 96 | 95.6 | 95.3 | 86.7 | 84.9 | 79.5 | 14 | 7 |  |  |  | 11787.1102 | 9325 |  |  |  | 4600 | 5980 | 1546 |  | 3909 | F | 78 | 103 | D | CF | CF
** Safe Stall Times quoted are values which will not in any way cause damage or reduction in life to the rotor, stator or bearings.
*** Subject to change at any time. Please confirm with factory prior to application on constant torque loads
**** Note - 350HP 1200RPM motor is 1.0SF

## Calculations
Look-up Table for Various Control Types
Flow | 0% | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
D. damper | 33.2% | 44% | 54% | 63% | 71.5% | 79.5% | 86.3% | 91% | 95% | 98% | 100%
Inlet vane | 35% | 37% | 40% | 44% | 48% | 53.1% | 60% | 66.8% | 76.4% | 89% | 100%
ASD | 0% | 0.1% | 0.8% | 2.7% | 6.4% | 12.5% | 21.6% | 34.3% | 51.2% | 72.9% | 100%
Pressure
D. damper | 110% | 115% | 120% | 135% | 130% | 128% | 125% | 118% | 110% | 105% | 100% | [8 empty] | 100% | 75% | 50% | 25% | 5% | 1%
Inlet vane | 0% | 1% | 4% | 9% | 16% | 25% | 36% | 49% | 64% | 81% | 100% | [8 empty] | 97.7% | 97.1% | 96.2% | 94% | 84% | 60%
ASD | 0% | 1% | 4% | 9% | 16% | 25% | 36% | 49% | 64% | 81% | 100%
| 30%: Discharge | Inlet
| 10%: Fixed; 30%: Damper; 40%: Actual | Vane | Actual | [6 empty] | ASD | Actual
| 10%: Speed; 30%: Characteristic; 40%: Motor; 50%: Motor Efficiency at Actual load | Characteristic | Motor | Motor Efficiency at Actual load | [5 empty] | Characteristic | Motor | Motor Efficiency at Actual load |  |  |  |  | ASD Efficiency at Load | [12 empty] | ASD & Motor
|  | KW Hrs |  | (% Load) | (% Load) | >75% | <75% | Actual | KW | KW Hrs |  | (% Load) | (% Load) | >75% | <75% | Actual | KW | KW Hrs |  | (% Load) | (% Load) | >75% | <75% | Actual | KW | >75% | >75% | >50% |  | >50% | >25% |  | >25% | >5% |  | >5% | >0% | >0% | Actual | KW | KW Hrs
0 | 100% | 0 |  | 100% | 100% | 92% | 0% | 92% | 405.4348 | 0 |  | 100% | 100% | 92% | 0% | 92% | 405.4348 | 0 |  | 100% | 100% | 92% | 0% | 92% | 405.4348 | 1 | 97.7% | 1 | 0 | 0% | 1 | 0 | 0% | 1 | 0 | 0% | 0 | 0% | 97.7% | 414.9793 | 0
2 | 90% | 810.8696 |  | 98% | 98% | 91.92% | 0% | 91.92% | 397.6719 | 795.3438 |  | 89% | 89% | 91.56% | 0% | 91.56% | 362.571 | 725.142 |  | 72.9% | 72.9% | 0% | 90.92% | 90.92% | 299.086 | 0 | 0% | 1 | 1 | 97.02% | 1 | 0 | 0% | 1 | 0 | 0% | 0 | 0% | 97.02% | 308.2585 | 616.517
6 | 80% | 2432.6087 |  | 95% | 95% | 91.8% | 0% | 91.8% | 386.0022 | 2316.0131 |  | 76.4% | 76.4% | 91.06% | 0% | 91.06% | 312.9635 | 1877.7807 |  | 51.2% | 51.2% | 0% | 90.05% | 90.05% | 212.0824 | 0 | 0% | 1 | 1 | 96.24% | 1 | 0 | 0% | 1 | 0 | 0% | 0 | 0% | 96.24% | 220.361 | 1322.1658
7 | 70% | 2838.0435 |  | 91% | 91% | 91.64% | 0% | 91.64% | 370.395 | 2592.7652 |  | 66.8% | 66.8% | 0% | 90.67% | 90.67% | 274.7971 | 1923.5795 |  | 34.3% | 34.3% | 0% | 89.37% | 89.37% | 143.1533 | 0 | 0% | 0 | 1 | 0% | 1 | 1 | 94.82% | 1 | 0 | 0% | 0 | 0% | 94.82% | 150.9763 | 1056.8343
3 | 60% | 1216.3043 |  | 86.3% | 86.3% | 91.45% | 0% | 91.45% | 351.9868 | 1055.9605 |  | 60% | 60% | 0% | 90.4% | 90.4% | 247.5664 | 742.6991 |  | 21.6% | 21.6% | 0% | 88.86% | 88.86% | 90.6644 | 0 | 0% | 0 | 1 | 0% | 0 | 1 | 0% | 1 | 1 | 100.6% | 0 | 0% | 100.6% | 90.0878 | 270.2635
5 | 50% | 2027.1739 |  | 79.5% | 79.5% | 91.18% | 0% | 91.18% | 325.2193 | 1626.0967 |  | 53.1% | 53.1% | 0% | 90.12% | 90.12% | 219.7672 | 1098.836 |  | 12.5% | 12.5% | 0% | 88.5% | 88.5% | 52.6836 | 0 | 0% | 0 | 1 | 0% | 0 | 1 | 0% | 1 | 1 | 97% | 0 | 0% | 97% | 54.313 | 271.565
1 | 40% | 405.4348 |  | 71.5% | 71.5% | 0% | 90.86% | 90.86% | 293.523 | 293.523 |  | 48% | 48% | 0% | 89.92% | 89.92% | 199.1103 | 199.1103 |  | 6.4% | 6.4% | 0% | 88.26% | 88.26% | 27.0486 | 0 | 0% | 0 | 1 | 0% | 0 | 1 | 0% | 1 | 1 | 94.56% | 0 | 0% | 94.56% | 28.6047 | 28.6047
0 | 30% | 0 |  | 63% | 63% | 0% | 90.52% | 90.52% | 259.6001 | 0 |  | 44% | 44% | 0% | 89.76% | 89.76% | 182.8431 | 0 |  | 2.7% | 2.7% | 0% | 88.11% | 88.11% | 11.4303 | 0 | 0% | 0 | 1 | 0% | 0 | 1 | 0% | 0 | 1 | 0% | 1 | 85.63% | 85.63% | 13.3482 | 0
0 | 20% | 0 |  | 54% | 54% | 0% | 90.16% | 90.16% | 223.4028 | 0 |  | 40% | 40% | 0% | 89.6% | 89.6% | 166.5179 | 0 |  | 0.8% | 0.8% | 0% | 88.03% | 88.03% | 3.3897 | 0 | 0% | 0 | 1 | 0% | 0 | 1 | 0% | 0 | 1 | 0% | 1 | 83.81% | 83.81% | 4.0446 | 0
0 | 10% | 0 |  | 44% | 44% | 0% | 89.76% | 89.76% | 182.8431 | 0 |  | 37% | 37% | 0% | 89.48% | 89.48% | 154.2356 | 0 |  | 0.1% | 0.1% | 0% | 88% | 88% | 0.42384 | 0 | 0% | 0 | 1 | 0% | 0 | 1 | 0% | 0 | 1 | 0% | 1 | 83.14% | 83.14% | 0.50982 | 0
0 | 0% | 0 |  | 33.2% | 33.2% | 0% | 89.33% | 89.33% | 138.6307 | 0 |  | 35% | 35% | 0% | 89.4% | 89.4% | 146.0291 | 0 |  | 0% | 0% | 0% | 88% | 88% | 0 | 0 | 0% | 0 | 1 | 0% | 0 | 1 | 0% | 0 | 1 | 0% | 1 | 83.04% | 83.04% | 0 | 0
24 | 10%: 9730.4348; 20%: (per Day); 90%: 8679.7023; 100%: (per Day) | [6 empty] | 6567.1477 | (per Day) | [21 empty] | 3565.9503 | (per Day)
| 10%: 3551608.6957; 20%: (per Year); 90%: 3168091.3231; 100%: (per Year) | [6 empty] | 2397008.899 | (per Year) | [21 empty] | 1301571.8512 | (per Year)
| 0%: Operating cost; 10%: 121820.1783; 20%: (per Year); 80%: Operating cost; 90%: 108665.5324; 100%: (per Year) | [5 empty] | Operating cost | 82217.4052 | (per Year) | [20 empty] | Operating cost | 44643.9145 | (per Year)
Motor Efficiency at Actual load | 30%: Fixed
>75% | 0%: <75%; 10%: Actual; 30%: Speed
92% | 0%: 0%; 10%: 92%; 30%: KW
405.4348
ASD Efficiency
100% | 0%: 75%; 10%: 50%; 20%: 25%; 30%: 5%; 40%: 1%
97.7% | 0%: 97.1%; 10%: 96.2%; 20%: 94%; 30%: 84%; 40%: 60%
>75% | 0%: <75%; 10%: <50%; 20%: Actual
97.7% | 0%: 0%; 20%: 97.7%